## Quote Runs
Job # | Type | Status | Template | Run File | Damper | Review | Serial | Size | Design | Class | Fan Type | Arrangement | % Width | Discharge | Rotation | Effective Wheel Dia | CFM | SP | BHP | RPM | Air Temp F | Max Temp F | Density | Max HP | Max RPM | Tip Speed FPM | Shaft Dia | Brg Centers | Critical Speed RPM | Shaft Length | OH | BX | STB | TG&P | STH | Bearing Size | Bearing Series | Bearing L10 Hr | Drive Brg Mount | Drive Brg Static Lb | Other Brg Mount | Other Brg Static Lb | Brg Thrust Lb | Rotor WR2 | Rotor Max RPM | Rotor Material | Stress Ratio at Hub | Stress Ratio at Bearing | Housing Width (N) | Base to CL (F) | Blade Material | Blade Gauge | Sideplate Material | Sideplate Gauge | Backplate Material | Backplate Gauge | Liner Material | Liner Gauge | Wheel Material | Blades | Max RPM Wheel Only | Wheel Resonance CPM | Wheel Weight Lb | Wheel Thrust Lb | Wheel WR2 | Housing to Wheel CG | Housing to Hub Inlet Face | Sheave PD | Min Sheave PD | Motor Frame | Motor Position | Motor Enclosure | Motor Weight Lb | Housing Construction | Stiffeners | Fan Outlet Area FT2 | Inlet Box Size | Shaft Seal | Shaft Seal Height | Flanged Inlet | Total Weight Lb | Total Price | Hub | Coupling | Drive | Engineering Approval | FEA Analysis | Non-Std Wheel Materials | Shrink Fit | Factory Run Test | Hub Tube Gauge | Hub Tube Material | Hub Flanges Gauge | Hub Flanges Material | Hub Centers Material | Hub Bore | Hub OD | Hub Bushing | Coupling Max Shaft Dia | Coupling Min Shaft Dia | Coupling Nom Shaft Dia | Coupling Keyway | Box B | Box C | Inlet Box Angle | Inlet Cone | Safety Guard | Other | Summary | Folder
400076 | GENERAL LINE | OK | cbc_qt_run_text | 369-21-1258 - QT Run.txt |  |  | 400076 | 13 | 16A |  |  | 9S | 100.0 | BAU | CW | 22 5/8 | 5000 | 15.00 | 19.2 | 2731 | 250 | 250 | 0.0557 | 30.0 | 2800 |  | 1 15/16 | 23 | 3476 | 41 15/16 | 9.65 | 9 5/8 | 6 7/8 |  |  | 1 15/16 | LINK BELT SERIES 200 | 47882 | FIXED | 301 | FIXED | 53 | 0 | 12 | 2896 | A240 304 SS | 0.24 | 0.57 | [10 empty] | A240 304L SS | 6 | 3301 | [6 empty] | 5.6 | 3.6 |  |  | TEFC | [12 empty] | Belt |  |  | Yes |  | Yes | [5 empty] | 1 15/16 | [11 empty] | Ambient Temp F=70 | Size=13; Design=16A; Arrangement=9S; % Width=100.0; Discharge=BAU; Rotation=CW; CFM=5000; SP=15.00; BHP=19.2; RPM=2731; Max Temp F=250; Effective Wheel Dia=22 5/8; Wheel Material=A240 304L SS; Blades=6; Shaft Dia=1 15/16; Brg Centers=23; Critical Speed RPM=3476; BX=9 5/8; STB=6 7/8; OH=9.65; Bearing Size=1 15/16; Bearing Series=LINK BELT SERIES 200; Motor Enclosure=TEFC; Drive=Belt | Open
400426 | HDX | OK | pdf_vision | QT RUN.pdf |  |  | SN400426 | 9312 | 1903 |  |  | 3D2 | 80.0 | 270 | CW | 98 3/16 | 323551 | 23.89 | 1474.0 | 975 | 248 | 300 | 0.0530 | 1600.0 | 1000 |  | 17 1/2 | 203 9/16 | 1439 | [6 empty] | 5 15/16 | LINK BELT SERIES 6800 | 400000 | [5 empty] | 52146 | 1002 | [29 empty] | SK-9-236 HI PRESSURE, 21 IN. CENTERS | [7 empty] | 19-5-2272, CAST STEEL | FALK T10, SIZE 1140T, BORE 5 3/4 | [23 empty] | Manufacturer=CHICAGO BLOWER CORP; Supplier=WELLS TECHNOLOGY; 6105 DW REF; Ambient Temp F=90; Wheel Weight W/O Hub=48232; WR2 Weight=4750; Hub Weight=774; Hub WR2 Weight=1116; Coupling Ref=SKE-9-356; Shaft Bore At Fan Shaft Half Coupling=5.7500; Max Shaft Diameter At Fan Shaft Half Coupling=5.7495; Min Shaft Diameter At Fan Shaft Half Coupling=5.7480; Shaft End Cut Down=5 3/4; Bearing Type=DRIVE-FIXED; Outlet Dimensions=106 1/2 IN. x 106 7/16 IN.; Box Dimensions=168 1/4 IN. x 35 3/8 IN.; Pedestals=B19-0-378; Pedestal Weight=892; Soleplate Weight=558; Insulation Studs Qty=1156; Pier Loads Inboard=10443; Pier Loads Outboard=10108 | Bearing L10 Hr=400000; Bearing Series=LINK BELT SERIES 6800; Bearing Size=5 15/16; Bearing Type=DRIVE-FIXED; Max Shaft Diameter At Fan Shaft Half Coupling=5.7495; Min Shaft Diameter At Fan Shaft Half Coupling=5.7480; Shaft Bore At Fan Shaft Half Coupling=5.7500; Shaft Dia=17 1/2; Shaft End Cut Down=5 3/4; Effective Wheel Dia=98 3/16; Wheel Weight W/O Hub=48232; Hub=19-5-2272, CAST STEEL | Open
400488 | HDX | OK | pdf_vision | QT RUN.pdf |  |  | SN400488 | 4900 | 5500 |  |  | 4S1 | 100.0 PCT | TH | CW | 49 3/4 | 23244 FPM | 28.90 SP | 187.2 BHP | 1780 RPM | 90 F | 150 F | 0.0649 | 200.0 | 1800 | 23444 FPM | [24 empty] | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 (7) | [26 empty] | 49-5-145-A BORE 3 3/8 (CAST STEEL) | [24 empty] | Wheel Weight=297 LB; Thrust=349 LB; WR2=547 LB-FT2; Outlet=20 1/4 IN. X 44 3/4 IN. (514 MM X 1137 MM); Box=66 3/4 IN. X 21 1/16 IN. (1695 MM X 535 MM); Base=447T FR MOTOR | Backplate Material=ASTM A1011-HSLAS; Blade Material=ASTM A1011-HSLAS; Sideplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 (7); Blade Gauge=0.135 (10); Sideplate Gauge=0.135 (10); Effective Wheel Dia=49 3/4; Wheel Weight=297 LB; Hub=49-5-145-A BORE 3 3/8 (CAST STEEL); % Width=100.0 PCT; Air Temp F=90 F; Arrangement=4S1 | Open
400534 | HDX | OK | pdf_vision | QT RUN CO#1.pdf |  |  | SN400534 | 5414 | 5500 |  |  | 7SL | 100.0 | TH | CCW |  | 45566 | 26.72 | 255.3 | 1780 | 105 | 105 | 0.0648 |  | 1800 | 24622 | 3 15/16 | 55 13/16 | 3161 | 67.69 | 45.12 | 12.58 | 8.88 |  |  | 2 15/16 | 6800 | [13 empty] | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 (7) | ASTM A572 X-TEN | 3/8 |  |  | CAST STEEL | [23 empty] | 23-5-424 | FALK T10, SIZE 1100T | DRIVE-FIXED | [23 empty] | Backplate Material=ASTM A572 X-TEN; Blade Material=ASTM A1011-HSLAS; Sideplate Material=ASTM A1011-HSLAS; Wheel Material=CAST STEEL; Backplate Gauge=3/8; Blade Gauge=0.135 (10); Sideplate Gauge=0.179 (7); Bearing Series=6800; Bearing Size=2 15/16; Shaft Dia=3 15/16; Shaft Length=67.69; Hub=23-5-424 | Open
400566 | HDX | OK | pdf_vision | QT RUN CO#1.pdf |  |  | SN400566 | 5100 | 2315B | KEYERA; CCF1 | JOHN ZINK, 9315533 COMBUSTION AIR FAN | 8S1 | 55.0 PCT | TAU | CW | 58 5/8 | 18427 CPM | 19.30 IN. WC | 111.2 BHP | 1180 RPM | 90 F | 82 F | 0.0696 | 200.0 | 1200 | 18425 FPM | 2 15/16 | 15 | 2553 RPM | 36 5/16 | 10.00 | 10 9/16 | 7 3/4 | 68 | 2.31 | 2 15/16 | LINK BELT SERIES 6800 | 400000 | [12 empty] | ASTM A240 304L SS | 1/4 | ASTM A240 304L SS | 1/4 | ASTM A240 304L SS | 5/16 |  |  | CAST 304L | [23 empty] | 49-5-149-H BORE 2 11/16 | THOMAS 71 SIZE 412 BORE 2.938 | [23 empty] | Coupling Ref=SKE-9-478 | Backplate Material=ASTM A240 304L SS; Blade Material=ASTM A240 304L SS; Sideplate Material=ASTM A240 304L SS; Wheel Material=CAST 304L; Backplate Gauge=5/16; Blade Gauge=1/4; Sideplate Gauge=1/4; Bearing L10 Hr=400000; Bearing Series=LINK BELT SERIES 6800; Bearing Size=2 15/16; Shaft Dia=2 15/16; Shaft Length=36 5/16 | Open
400567 | HDX | OK | cbc_qt_run_text | Qt Run CO#1.txt |  |  | 400567 | 20.000 | 1904 |  |  | 8S | 80.0 | TH | CW | 22 | 6221 | 14.90 | 18.5 | 3550 | 293 | 293 | 0.0514 | 20.0 | 3600 | 20735 | 2 7/16 | 12 | 5309 | 27 7/16 | 9.54 | 13 11/16 | 4 1/8 |  | 1.25 | 2 7/16 | LINK BELT SERIES 300 | 400000 | FIXED | -51 | FIXED | 176 | 71 | 28 | 3600 | A240 304 SS | 0.08 | 0.03 | 12 3/4 |  | ASTM A240 304L SS | 0.060 (16) | ASTM A240 304L SS | 0.105 (12) | ASTM A240 304L SS | 1/4 |  |  |  | 10 | 4113 | 7300 | [7 empty] | 256T |  | TEFC | 312 | 3/16 A240 304L SS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 2.020 |  | Included | 3.00 | Included |  |  | 19-5- |  | Direct |  |  | Yes | Yes | Yes | [5 empty] | 2 3/16 |  |  | 1.6870 | 1.6860 | 1.6875 | 0.3750 X 0.1875 |  |  |  |  | Yes | Ambient Temp F=90; Discharge Height (A)=22 13/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=1 1/2; Discharge Flange to CL (E)=18 1/4; Base Width (F)=32; Shaft Height (H)=19; Total Vert Height (TV)=43 1/8; Max Right of CL to Hsg (RH)=18 1/4; Max Left of CL to Disch (LH)=19 13/16; Base Flange to CL (D)=56 1/16; Drive End of Shaft to CL (K)=29 13/16; Mtg Flange to CL (LR)=8 3/8 | Size=20.000; Design=1904; Arrangement=8S; % Width=80.0; Discharge=TH; Rotation=CW; CFM=6221; SP=14.90; BHP=18.5; RPM=3550; Max Temp F=293; Effective Wheel Dia=22; Blade Material=ASTM A240 304L SS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A240 304L SS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A240 304L SS; Backplate Gauge=1/4; Hub=19-5-; Blades=10; Shaft Dia=2 7/16; Brg Centers=12; Critical Speed RPM=5309; BX=13 11/16; STB=4 1/8; OH=9.54; STH=1.25; Bearing Size=2 7/16; Bearing Series=LINK BELT SERIES 300; Housing Width (N)=12 3/4; Motor Frame=256T; Motor Enclosure=TEFC; Drive=Direct | Open
400934 | HD-PFD-IAF | CHECK VISION | pdf_vision | QT RUN-GMH.pdf |  |  | POWER FLAME D1902 | 3000 | 1902 |  | PACKAGED FORCED DRAFT FAN | 4S | 95.0 | DISCH BAU, ROT CW | CW | 52 | 20000 | 5.8, 144.2 BHP | 144.2 | 3400 | 70 | 70 | 0.0750 | 150.0 | 4400 | 26704 | 1 7/8 | [7 empty] | 1.94 |  | SIDEPL, SPUN | [13 empty] | ASTM A1011-HSLAS | 0 10(12) | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  | A1011-HSLAS | 10 | 3481 | 5070 | 184 | 244 | 165 | 4.40 | 4.44 |  |  | 444TS |  |  | 1515 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 4.769 |  | Not included |  | Yes | 2760 | 19948 | 19-5-1056, Q2 BUSHING 2 3/8, C. IRON |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q2 BUSHING 2 3/8 | [9 empty] | Ambient Temp F=70; Wheel Weight=184 LB; Thrust=244 LB; WR2 Weight=165 LB-FT2 | Size=3000; Design=1902; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S; % Width=95.0; Discharge=DISCH BAU, ROT CW; Rotation=CW; CFM=20000; SP=5.8, 144.2 BHP; BHP=144.2; RPM=3400; Max Temp F=70; Effective Wheel Dia=52; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0 10(12); Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Wheel Material=A1011-HSLAS; Hub=19-5-1056, Q2 BUSHING 2 3/8, C. IRON; Blades=10; Shaft Dia=1 7/8; STH=1.94; Bearing Series=SIDEPL, SPUN; Motor Frame=444TS; Drive=Motor mounted | Open
401012 | GENERAL LINE | OK | cbc_qt_run_text | QT Run.txt |  |  | 401012 | 13 | 16A | 4 |  | 9H | 100.0 | TH | CW | 22 5/8 | 6200 | 30.00 | 46.9 | 3393 | 100 | 100 | 0.0710 | 50.0 | 3393 | 20098 | 2 3/16 | 14 | 4257 | 37 7/8 | 11.78 | 11 3/4 | 9 |  |  | 2 3/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 833 | FIXED | 197 | 0 | 10 | 3468 | A240 304 SS | 0.19 | 0.70 |  |  | ASTM A240 304L SS | 0.135 (10) | [7 empty] | 6 | 3468 | 23780 | [5 empty] | 4.5 | 3.0 | [15 empty] | Belt | Required |  | Yes |  | Yes | 1/2 | ASTM A240 304L SS | 3/8 | ASTM A240 304L SS | ASTM A240 304L SS | 2 3/16 | 5.00 | [10 empty] | Ambient Temp F=70 | Size=13; Design=16A; Arrangement=9H; % Width=100.0; Discharge=TH; Rotation=CW; Class=4; CFM=6200; SP=30.00; BHP=46.9; RPM=3393; Max Temp F=100; Effective Wheel Dia=22 5/8; Blade Material=ASTM A240 304L SS; Blade Gauge=0.135 (10); Blades=6; Shaft Dia=2 3/16; Brg Centers=14; Critical Speed RPM=4257; BX=11 3/4; STB=9; OH=11.78; Bearing Size=2 3/16; Bearing Series=LINK BELT SERIES 6800; Drive=Belt | Open
401069 | HD-PFD-IAF | OK | cbc_qt_run_text | 401069 Quote Run.docx |  |  | 401069 | 4014 | 1903 |  | PACKAGED FORCED DRAFT FAN | 4S | 90.0 | TH | CW | 42 1/4 | 25200 | 22.00 | 104.2 | 1770 | 70 | 70 | 0.0750 | 125.0 | 1800 | 19916 | [8 empty] | 2.50 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 1/4 |  |  |  | 10 | 2121 | 2650 | 257 | 255 | 362 | 4.85 | 6.38 |  |  | 444T |  |  | 1515 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 8.510 |  | Not included |  | Yes |  |  | 19-5-16 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 3 3/8 | [11 empty] | Ambient Temp F=70 | Size=4014; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S; % Width=90.0; Discharge=TH; Rotation=CW; CFM=25200; SP=22.00; BHP=104.2; RPM=1770; Max Temp F=70; Effective Wheel Dia=42 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Hub=19-5-16; Blades=10; STH=2.50; Motor Frame=444T; Drive=Motor mounted | Open
401078 | HDX | OK | pdf_vision | QT RUN.pdf |  |  | SN401078 | 4800 | 2305B |  |  | 8S | 100.0 | TH | CW | 50 3/8 | 23000 | 41.00 | 239.5 | 1780 | 100 | 100 | 0.0695 | 300.0 | 1800 | 23750 | 2 15/16 | 12 1/2 | 3607 | 32 | 9.02 | 10 7/16 | 8 7/8 | 1.5 | 1.94 | 2 15/16 | 6800 | 2136673 | FIXED | -258 | FLOAT | 868 | 0 | 1018 | 2271 | 1045 STEEL | 0.76 | 0.55 |  |  | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  | CAST STEEL | 11 | 2308 | 3980 | [7 empty] | 449T |  | ODP | 2600 | 3/16 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 2.241 |  |  |  |  | 6068 | 58785 | HUB 23-5-424 BORE 2 11/16 | FAIK T10, SIZE 1100T, BORE 2.938 | Direct |  |  |  | Yes | [6 empty] | 2 11/16 |  |  | 2.9370 | 2.9355 | 2.9375 | 0.7500 X 0.3750 |  |  |  |  | Yes | Ambient Temp F=100 | Size=4800; Design=2305B; Arrangement=8S; % Width=100.0; Discharge=TH; Rotation=CW; CFM=23000; SP=41.00; BHP=239.5; RPM=1780; Max Temp F=100; Effective Wheel Dia=50 3/8; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Wheel Material=CAST STEEL; Hub=HUB 23-5-424 BORE 2 11/16; Coupling=FAIK T10, SIZE 1100T, BORE 2.938; Blades=11; Shaft Dia=2 15/16; Brg Centers=12 1/2; Critical Speed RPM=3607; BX=10 7/16; STB=8 7/8; OH=9.02; STH=1.94; Bearing Size=2 15/16; Bearing Series=6800; Motor Frame=449T; Motor Enclosure=ODP; Drive=Direct | Open
401078 | HDX | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | SN401078 | 4800 | 2305B |  |  | 88 | 100.0 | DISCH TH | ROT CW | 50 3/8 | 23000 | 41.00 | 239.5 | 1780 | 100 | 100 | 0.0695 | 300.0 | 1800 | 23750 | 2 15/16 | 12 1/2 | 3607 | 32 | 9.02 | 10 7/16 | 8 7/8 | M1.5 | 1.94 | 2 15/16 | 6800 | 213673 | FIXED | -258 | FLOAT | 868 | 0 | 1018 | 2271 | 1045 STEEL | 0.76 | 0.55 |  |  | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  | CAST STEEL | 11 | 2308 | 3980 | [7 empty] | 449T |  | ODP | 2600 | 3/16 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 2.241 |  |  |  |  | 6068 | 58785 | 23-5-424 BORE 2 11/16 | FAIK T10, SIZE 1100T, BORE 2.938 | DRIVE-FIXED |  |  |  | Yes | [6 empty] | 2 11/16 |  |  | 2.9370 | 2.9355 | 2.9375 | 0.7500 X 0.3750 |  |  |  |  | Yes | Ambient Temp F=100 F | Size=4800; Design=2305B; Arrangement=88; % Width=100.0; Discharge=DISCH TH; Rotation=ROT CW; CFM=23000; SP=41.00; BHP=239.5; RPM=1780; Max Temp F=100; Effective Wheel Dia=50 3/8; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Wheel Material=CAST STEEL; Hub=23-5-424 BORE 2 11/16; Coupling=FAIK T10, SIZE 1100T, BORE 2.938; Blades=11; Shaft Dia=2 15/16; Brg Centers=12 1/2; Critical Speed RPM=3607; BX=10 7/16; STB=8 7/8; OH=9.02; STH=1.94; Bearing Size=2 15/16; Bearing Series=6800; Motor Frame=449T; Motor Enclosure=ODP; Drive=DRIVE-FIXED | Open
401195 | HD-PFD-IAF | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | 309261 | 4412 | 1904 |  |  | 4SL | 65.0 | BAD | CCW | 48 15/16 | 2500 | 25.50 | 148.3 | 1780 | 70 | 70 | 0.0675 | 150 | 1800 | 23067 | 1 7/8 | 22.81 | [6 empty] | 2.81 | SK-9-105 | [14 empty] | ASTM A1008 CS | 0.060 (16) | ASTM A1011 CS | 0.179 (7) | ASTM CQ HRS-A36 | 3/8 |  |  | CAST IRON | 10 | 1800 |  | 448 |  | 850 | 4.66 | [5 empty] | ODP | 1515 | 1/4 C.O. HRS | SK-9-236 HI | 9.448 |  | Not included |  |  | 7775 | 70549 | 19-5-289 BORE 3 3/8 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 3 3/8 | [6 empty] | 57 | 57 | 1 |  |  | Ambient Temp F=90; Wheel Weight=448; WR2 Weight=850 LB-FT2; Thrust=436 LB; Outlet N x A=26 7/8 IN. x 50 5/8 IN.; Box B x C=57 IN. x 57 IN.; Base=4440; Motor Mounting=INCLUDED; Split Housing=1/4 C.O. HRS; Special Inlet Box=57.00 X 57.00; Damper Frame=5 AXLES 64.5 L., 12 IN. FRAME; Damper Frame Area=22.562 FT2; Damper Frame Thickness=1/4; Manual Control=OPERATING HANDLE LOC. 1, POS. 270; Fan Outlet Area=9.448 FT2 | Size=4412; Design=1904; Arrangement=4SL; % Width=65.0; Discharge=BAD; Rotation=CCW; CFM=2500; SP=25.50; BHP=148.3; RPM=1780; Max Temp F=70; Effective Wheel Dia=48 15/16; Blade Material=ASTM A1008 CS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.179 (7); Backplate Material=ASTM CQ HRS-A36; Backplate Gauge=3/8; Wheel Material=CAST IRON; Hub=19-5-289 BORE 3 3/8; Blades=10; Shaft Dia=1 7/8; Brg Centers=22.81; STH=2.81; Bearing Size=SK-9-105; Motor Enclosure=ODP; Drive=Motor mounted | Open
401217 | GENERAL LINE | CHECK VISION | pdf_vision | QUOTE RUN.pdf |  |  | 352450 | 4412 | 6195 |  |  | 48 | 90.0 | UB | CCW | 42 1/4 | 4000 | 12.00 | 119.8 | 1770 | 70 | 70 | 0.0750 | 125.0 | 1800 | 21914 | 2.81 | [7 empty] | 2.81 | [15 empty] | ASTM A572 X-TEN | 5/16 | ASTM A572 X-TEN | 3/16 | ASTM A572 X-TEN | 5/16 |  |  | ASTM A6 XF-100 | 10 | 2351 | 3400 | 403 | 294 | 672 | 5.54 | 7.19 |  |  | 444T |  |  | 1515 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 10.371 |  | Not included |  | Yes | 4372 | 40083 | BORE 3 3/8 CAST IRON |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 3 3/8 | [9 empty] | SK-19-72 |  | Ambient Temp F=90; Wheel Weight=403; Bearing Type=10 BLADES; Bearing Capacity=3400 CPM; Housing Inlet Face=7.19 IN; Wheel Weight Total=403 LB; Thrust=294 LB; Motor Base=444T FR MOTOR; Outlet=29 1/2 IN. X 50 5/8 IN. | Size=4412; Design=6195; Arrangement=48; % Width=90.0; Discharge=UB; Rotation=CCW; CFM=4000; SP=12.00; BHP=119.8; RPM=1770; Max Temp F=70; Effective Wheel Dia=42 1/4; Blade Material=ASTM A572 X-TEN; Blade Gauge=5/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=3/16; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Wheel Material=ASTM A6 XF-100; Hub=BORE 3 3/8 CAST IRON; Blades=10; Shaft Dia=2.81; STH=2.81; Motor Frame=444T; Drive=Motor mounted | Open
401221 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 401221 | 4014 | 6195 |  |  | 4S | 100.0 | UB | CW | 38 1/4 | 30240 | 14.00 | 82.8 | 1770 | 70 | 70 | 0.0750 | 100.0 | 1770 | 19491 | [8 empty] | 2.50 | [15 empty] | ASTM A6 XF-100 | 3/16 | ASTM A1011-HSLAS | 0.135 (10) | ASTM A572 X-TEN | 1/4 |  |  |  | 10 | 2346 | 3110 | 267 | 190 | 387 | 5.33 | 6.38 |  |  | 405T |  | TEFC | 1575 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 8.828 |  | Not included |  | Included | 3773 | 32851 | 19-5-16 |  | Motor mounted |  |  | Yes |  | Yes | [5 empty] | 2 7/8 | [11 empty] | Ambient Temp F=70 | Size=4014; Design=6195; Arrangement=4S; % Width=100.0; Discharge=UB; Rotation=CW; CFM=30240; SP=14.00; BHP=82.8; RPM=1770; Max Temp F=70; Effective Wheel Dia=38 1/4; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=19-5-16; Blades=10; STH=2.50; Motor Frame=405T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
401233 | HDX | OK | cbc_qt_run_text | QT Run.pdf |  |  | 401233 | 4200 | 4900 |  |  | 7S1 | 100.0 | TH | CW |  | 4800 | 25.00 | 35.0 | 1780 | 80 | 100 | 0.0713 | 50.0 | 1800 | 19792 | 2 3/16 | 29 | 3750 |  |  |  | 6.50 |  | 1.76 | 1 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | 231 | FLOAT | 74 | 0 | 299 | 2532 | 1045 STEEL | 0.26 | 0.32 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A572 X-TEN | 1/4 |  |  |  | 11 | 2532 | 3170 | [7 empty] | 326T |  |  | 610 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 0.518 |  |  |  |  | 3004 | 49370 | 49-5-145- | FALK T10 | Direct |  |  |  | Yes | Yes | [5 empty] | 2 3/16 |  |  | 1.9370 | 1.9360 |  | 0.5000 X 0.2500 | 43 3/8 | 14 1/4 | 270 |  | Yes | Ambient Temp F=90 | Size=4200; Design=4900; Arrangement=7S1; % Width=100.0; Discharge=TH; Rotation=CW; CFM=4800; SP=25.00; BHP=35.0; RPM=1780; Max Temp F=100; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=49-5-145-; Coupling=FALK T10; Blades=11; Shaft Dia=2 3/16; Brg Centers=29; Critical Speed RPM=3750; STB=6.50; STH=1.76; Bearing Size=1 15/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=326T; Drive=Direct | Open
401266 | HD-PFD-IAF | CHECK VISION | pdf_vision | QUOTE RUN-SIGNED - 10-05-21.pdf |  |  | SK-9-105 | 2412 | 1904 |  | PACKAGED FORCED DRAFT FAN | 481 | 105.0 | BH | CCW | 26 15/16 | 15851 | 25.83 | 84.6 | 3575 | 100 | 100 | 0.0653 | 125.0 | 3600 | 25400 | [8 empty] | 1.62 | [15 empty] | ASTM A1011-HSLAS | 0.048 (18) | ASTM A1011-HSLAS | 0.179 (7) | ASTM CQ HRS A36 | 1/4 |  |  | ASTM A1011-HSLAS | 10 | 3929 |  | 109 | 160 | 68 | 3.60 | 4.12 |  |  | 444TS |  |  | 1515 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 3.322 | 27.000 | Not included |  |  |  |  | 19-5-1056, Q2 BUSHING 2 3/8, C. IRON |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q2 BUSHING 2 3/8 |  |  |  |  | 48 1/2 | 10 5/16 | 270 |  |  | Ambient Temp F=70; Wheel Weight=109; WR2 Weight=68 LB-FT2; Thrust=160 LB; Box Weight=2412 Box OK; Inlet Velocity=2.78 - 5496 ft/min; Outlet N x A=17 1/8 IN. X 27 15/16 IN. (435 MM X 710 MM); Box B x C=48 1/2 IN. X 10 5/16 IN. (1232 MM X 262 MM) | Size=2412; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=481; % Width=105.0; Discharge=BH; Rotation=CCW; CFM=15851; SP=25.83; BHP=84.6; RPM=3575; Max Temp F=100; Effective Wheel Dia=26 15/16; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.048 (18); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 (7); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Wheel Material=ASTM A1011-HSLAS; Hub=19-5-1056, Q2 BUSHING 2 3/8, C. IRON; Blades=10; STH=1.62; Motor Frame=444TS; Drive=Motor mounted | Open
401266 | HD-PFD-IAF | CHECK VISION | pdf_vision | QUOTE RUN - 06-30-21.pdf |  |  | 275-21-1555 | 2412 | 1904 | 105.0 | ROT CW | 451 | 105.0 | PCT | DISCH UB | 26 15/16 | 15851 | 25.83 | 84.6 | 3575 | 100 | 100 | 0.0650 | 125.0 | 3600 | 25400 | [8 empty] | 1.62 | [15 empty] | ASTM A1011-HSLAS | 0.048 (18) | ASTM A1011-HSLAS | 0.179 (7) | ASTM A572 X-TEN | 1/4 |  |  |  | 10 | 3929 |  | 109 | 160 | 68 | 3.60 | 4.12 | [5 empty] | 1515 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 3.322 | 27.000 | Not included |  |  |  |  | 19-5-1056 |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q2 BUSHING 2 3/8 |  |  |  |  | 48 1/2 | 10 5/16 | 45 |  |  | Ambient Temp F=-15; Wheel Weight=109; Thrust=160 LB; WR2=68 LB-FT2 | Size=2412; Design=1904; Fan Type=ROT CW; Arrangement=451; % Width=105.0; Discharge=PCT; Rotation=DISCH UB; Class=105.0; CFM=15851; SP=25.83; BHP=84.6; RPM=3575; Max Temp F=100; Effective Wheel Dia=26 15/16; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.048 (18); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 (7); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=19-5-1056; Blades=10; STH=1.62; Drive=Motor mounted | Open
401331 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN WITHOUT COOLING WHEEL.txt |  |  | 401331 | 4014 | 1903 |  | PACKAGED FORCED DRAFT FAN | 8S | 90.0 | BAU | CW | 42 1/4 | 27000 | 12.00 | 64.7 | 1770 | 250 | 250 | 0.0469 | 100.0 | 1800 | 19916 | 2 3/16 | 14 | 3190 | 29 11/16 | 8.04 | 16 9/16 | 7 1/4 | 32 | 2.50 | 2 3/16 | LINK BELT SERIES 300 | 400000 | FIXED | -90 | FIXED | 375 | 255 | 363 | 1822 | 1045 STEEL | 0.59 | 0.50 | 26 3/4 |  | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 1/4 |  |  |  | 10 | 2121 | 2650 | [7 empty] | 405T |  |  | 1260 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 8.510 |  |  |  | Yes |  |  | 19-5-1057 | FALK T10 | Direct |  |  |  |  | Yes | [7 empty] | Q1 BUSHING 2 3/16 | 2.1870 | 2.1860 | 2.1875 | 0.5000 X 0.2500 |  |  |  |  | Yes | Ambient Temp F=70; Discharge Height (A)=45 13/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=30; Base Width (F)=55; Shaft Height (H)=46 7/16; Total Vert Height (TV)=75 15/16; Max Right of CL to Hsg (RH)=36 1/4; Max Left of CL to Disch (LH)=55; Base Flange to CL (D)=71 1/16; Drive End of Shaft to CL (K)=37 13/16; Mtg Flange to CL (LR)=16 3/8 | Size=4014; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=8S; % Width=90.0; Discharge=BAU; Rotation=CW; CFM=27000; SP=12.00; BHP=64.7; RPM=1770; Max Temp F=250; Effective Wheel Dia=42 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Hub=19-5-1057; Coupling=FALK T10; Blades=10; Shaft Dia=2 3/16; Brg Centers=14; Critical Speed RPM=3190; BX=16 9/16; STB=7 1/4; OH=8.04; STH=2.50; Bearing Size=2 3/16; Bearing Series=LINK BELT SERIES 300; Housing Width (N)=26 3/4; Motor Frame=405T; Drive=Direct | Open
401378 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.txt |  |  | 401378 | 2700 | 1904 |  | PACKAGED FORCED DRAFT FAN | 4S1 | 90.0 | BH | CW | 29 11/16 | 22000 | 21.00 | 121.3 | 3550 | 100 | 125 | 0.0700 | 236.0 | 3600 | 27992 | [8 empty] | 1.69 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 3/8 |  |  |  | 10 | 3962 |  | 172 | 236 | 140 | 3.59 | 4.19 |  |  | 444TS |  |  | 1515 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 3.817 | 33.000 | Not included |  |  |  |  | 19-5-1056 |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q2 BUSHING 2 3/8 |  |  |  |  | 59 1/2 | 12 9/16 | 10 |  |  | Ambient Temp F=70 | Size=2700; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S1; % Width=90.0; Discharge=BH; Rotation=CW; CFM=22000; SP=21.00; BHP=121.3; RPM=3550; Max Temp F=125; Effective Wheel Dia=29 11/16; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Hub=19-5-1056; Blades=10; STH=1.69; Motor Frame=444TS; Drive=Motor mounted | Open
401379 | HD-PFD-IAF | OK | pdf_vision | QT RUN.pdf |  |  | 401379 | 3000 | 1903 |  | PACKAGED FORCED DRAFT FAN | 8S1 | 95.0 | UB | CW | 31 1/2 | 29340 | 18.00 | 123.7 | 3400 | 283 | 333 | 0.0513 | 125.0 | 3400 | 28039 | 3 3/16 | 12 | 4723 | 33 3/8 | 10.95 | 16 3/4 | 7 1/2 | 76 | 1.94 | 3 3/16 | LINK BELT SERIES 300 | 40000 | FIXED | -162 | FIXED | 496 | 281 | 179 | 3562 | 1045 STEEL | 0.15 | 0.10 |  |  | ASTM A1011-HSLAS | 0.105 (12) | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  | CAST STEEL | 10 | 3562 | 5260 | [7 empty] | 444TS |  |  | 1515 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 4.769 | 36.500 |  |  |  | 3897 | 49117 | 19-5-11 | THOMAS 71 SIZE 350 | Direct |  | Required |  |  | Yes | [5 empty] | 3 3/16 | [6 empty] | 65 3/4 | 13 13/16 | 10 |  | Yes |  | Size=3000; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=8S1; % Width=95.0; Discharge=UB; Rotation=CW; CFM=29340; SP=18.00; BHP=123.7; RPM=3400; Max Temp F=333; Effective Wheel Dia=31 1/2; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Wheel Material=CAST STEEL; Hub=19-5-11; Coupling=THOMAS 71 SIZE 350; Blades=10; Shaft Dia=3 3/16; Brg Centers=12; Critical Speed RPM=4723; BX=16 3/4; STB=7 1/2; OH=10.95; STH=1.94; Bearing Size=3 3/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=444TS; Drive=Direct | Open
401380 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 401380 | 2700 | 6105 |  |  | 4S | 50.0 | DB | CW | 28 3/8 | 8350 | 35.20 | 68.0 | 3550 | 90 | 90 | 0.0697 | 75.0 | 3600 | 29391 | [8 empty] | 1.69 | [15 empty] | ASTM A6 XF-100 | 3/16 | ASTM A572 X-TEN | 3/16 | ASTM A572 X-TEN | 1/4 |  |  |  | 10 | 4375 | 11680 | 110 | 228 | 72 | 2.73 | 4.19 |  |  | 365TS |  |  | 920 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 19 IN. CENTERS | 3.257 |  | Not included |  | Yes | 1786 | 30721 | 19-5-1056 |  | Motor mounted |  |  | Yes |  | Yes | [7 empty] | Q2 BUSHING 1 7/8 | [7 empty] | SK-19-72 |  | Ambient Temp F=70 | Size=2700; Design=6105; Arrangement=4S; % Width=50.0; Discharge=DB; Rotation=CW; CFM=8350; SP=35.20; BHP=68.0; RPM=3550; Max Temp F=90; Effective Wheel Dia=28 3/8; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=3/16; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=19-5-1056; Blades=10; STH=1.69; Motor Frame=365TS; Drive=Motor mounted | Open
401395 | GENERAL LINE | OK | cbc_qt_run_text | QUOTE RUN.txt |  |  | 401395 | 18 | 36 | 1 |  | 4S | 110.0 | TH | CW |  | 9500 | 15.00 | 36.5 | 3500 | 70 | 70 | 0.0750 | 40.0 | 3600 | 18559 | [8 empty] | 1.86 | [15 empty] | ASTM A572 X-TEN | 5/16 | ASTM A1011 CS | 0.075 (14) | ASTM A1011 CS | 0.179 ( 7) |  |  |  | 12 | 3772 | 5910 | 72 | 51 | 24 | 3.92 | 5.49 | [15 empty] | 4-5-14 | [6 empty] | Yes | [5 empty] | 1 7/8 | [11 empty] | Ambient Temp F=70 | Size=18; Design=36; Arrangement=4S; % Width=110.0; Discharge=TH; Rotation=CW; Class=1; CFM=9500; SP=15.00; BHP=36.5; RPM=3500; Max Temp F=70; Blade Material=ASTM A572 X-TEN; Blade Gauge=5/16; Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.075 (14); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.179 ( 7); Hub=4-5-14; Blades=12; STH=1.86 | Open
401445 | HDX | CHECK VISION | pdf_vision | QT RUN-GMH.pdf |  |  | SN401445 | 6912 | 5500 |  |  | 781 | 100.0 | TH | CW | 70 1/4 | 28967 | 660.9 | 660.9 | 1480 | 105 | 130 | 0.0691 | 700.0 | 1575 | 28967 | 4 15/16 | 70 1/8 | 2468 |  |  |  | 10.62 |  | 2.81 | 3 15/16 | 6800 | 1068 | FIXED | 1073 | FLOAT | 416 | 0 | 4134 | 1681 |  | 0.36 | 0.66 |  |  | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 3/8 |  |  | CAST STEEL | 16 | 1681 | [10 empty] | ODP | 5200 | 3/8 C.Q. HRS | SK-9-236 HI PRESSURE, 18 IN. CENTERS | 12.665 |  | Included | 3.00 |  | 21517 | 189287 | 4 15/16 BORE | FALK T10, SIZE 110T | NON-NEMA MOTOR |  | Required |  | Yes | [6 empty] | 4 15/16 |  |  | 3.9370 | 3.9355 |  | 1.0000 X 0.5000 | 94 3/4 | 29 7/8 | 1177 | SK-55-11 | Yes | Ambient Temp F=90 | Size=6912; Design=5500; Arrangement=781; % Width=100.0; Discharge=TH; Rotation=CW; CFM=28967; SP=660.9; BHP=660.9; RPM=1480; Max Temp F=130; Effective Wheel Dia=70 1/4; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Wheel Material=CAST STEEL; Hub=4 15/16 BORE; Coupling=FALK T10, SIZE 110T; Blades=16; Shaft Dia=4 15/16; Brg Centers=70 1/8; Critical Speed RPM=2468; STB=10.62; STH=2.81; Bearing Size=3 15/16; Bearing Series=6800; Motor Enclosure=ODP; Drive=NON-NEMA MOTOR | Open
401667 | HDX | OK | pdf_vision | QT RUN REV A.pdf |  |  | SN401667 | 3300 | 1910 |  |  | 3D | 105.0 | CCW | CCW | 13052 | 40900 | 13.00 | 100.0 | 1780 | 110 | 110 | 0.0688 | 125.0 | 2070 | 19296 | 6 | 71 | 2995 |  |  |  | 13.00 |  |  | 2 15/16 | DODGE PLAIN SLEEVELOIL BEARINGS |  | FIXED | 441 | FIXED | 381 | 0 | 373 | 2139 | 1045 STEEL |  |  |  |  | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) |  |  |  |  | CAST IRON |  | 2375 | 3850 | [11 empty] | 3/16 C.Q. HRS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 11.437 |  |  |  | Yes |  |  | 19-5-127 | FALK T10, SIZE 1090T, BORE 2 15/16 | DRIVE-FIXED |  |  |  | Yes | [9 empty] | 2.9370 | 2.9355 | 2.9375 | 0.7500 X 0.3750 |  |  |  |  | Yes | Ambient Temp F=90; Centerplate Material=ASTM CQ HRS A36; Centerplate Gauge=1/4 | Size=3300; Design=1910; Arrangement=3D; % Width=105.0; Discharge=CCW; Rotation=CCW; CFM=40900; SP=13.00; BHP=100.0; RPM=1780; Max Temp F=110; Effective Wheel Dia=13052; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Wheel Material=CAST IRON; Hub=19-5-127; Coupling=FALK T10, SIZE 1090T, BORE 2 15/16; Shaft Dia=6; Brg Centers=71; Critical Speed RPM=2995; STB=13.00; Bearing Size=2 15/16; Bearing Series=DODGE PLAIN SLEEVELOIL BEARINGS; Drive=DRIVE-FIXED | Open
401810 | HDX | OK | pdf_vision | QT RUN.pdf |  |  | SN401810 | 5100 | 2315B |  | JOHN ZINK, 9315533 SPARE COMBUSTION AIR FAN; KEYERA | 8S1 | 55.0 | DISCH TAU | ROT CW | 58 5/8 | 7100 | 19.30 | 111.2 | 1180 | 90 | 82 | 0.0696 | 200.0 | 1200 | 18425 | 2 15/16 | 15 | 2553 | 36 5/16 | 10.00 | 10 9/16 | 7 3/4 | MI.5 | 3.00 | 2 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -375 | FLOAT | 1153 | 0 | 1764 | 1756 | A240 304 SS | 0.70 | 0.49 |  |  | ASTM A240 304L SS | 1/4 | ASTM A240 304L SS | 1/4 | ASTM A240 304L SS | 5/16 |  |  |  | 11 | 1756 | 7100 | [7 empty] | 449T |  | TEFC | 3250 | 3/16 A240 304L SS | SK-9-236 HI PRESSURE, 22 IN. CENTERS |  |  | Included | 3.00 |  |  |  | 49-5-149-H BORE 2 11/16 CAST 304L | THOMAS 71 SIZE 412 BORE 2.938 | Direct |  |  | Yes | Yes | Yes | [5 empty] | 2 11/16 |  |  | 2.9370 | 2.9355 | 2.9375 | 0.7500 X 0.3750 | 52 5/8 | 17 1/4 | 742 |  | Yes | Ambient Temp F=90; Base=4497 FR MOTOR | Size=5100; Design=2315B; Fan Type=JOHN ZINK, 9315533 SPARE COMBUSTION AIR FAN; KEYERA; Arrangement=8S1; % Width=55.0; Discharge=DISCH TAU; Rotation=ROT CW; CFM=7100; SP=19.30; BHP=111.2; RPM=1180; Max Temp F=82; Effective Wheel Dia=58 5/8; Blade Material=ASTM A240 304L SS; Blade Gauge=1/4; Sideplate Material=ASTM A240 304L SS; Sideplate Gauge=1/4; Backplate Material=ASTM A240 304L SS; Backplate Gauge=5/16; Hub=49-5-149-H BORE 2 11/16 CAST 304L; Coupling=THOMAS 71 SIZE 412 BORE 2.938; Blades=11; Shaft Dia=2 15/16; Brg Centers=15; Critical Speed RPM=2553; BX=10 9/16; STB=7 3/4; OH=10.00; STH=3.00; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=449T; Motor Enclosure=TEFC; Drive=Direct | Open
401819 | HDX | OK | pdf_vision | QT RUN REV B.pdf |  |  | SN401819 | 4412 | 1904 |  |  | 3S | 110.0 | CCW | CCW | 48 15/16 | 4000 | 86.8 | 86.8 | 1180 | 80 | 100 | 0.0736 | 100.0 | 1200 | 15378 | 2 3/16 | 40 1/8 | 1933 | 48.75 | 9.38 | 33.88 | 19.31 | 6.25 | 2.81 | 2 3/16 | LINK BELT SERIES 300 | 103597 | FIXED | 368 | FIXED | 112 | 0 | 738 | 1393 | 1045 STEEL | 0.73 | 0.67 |  |  | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A572 X-TEN | 1/4 |  |  | CAST IRON | 10 | 1393 | 1740 | [11 empty] | 1/4 C.Q. HRS | SK-9-236 MED PRESSURE, 30 IN. CENTERS | 11.162 |  |  |  | Yes | 2406 | 46831 | 19-5-289 | FALK G20, SIZE 1025G, BORE 2 3/16 NOT INCL. | Direct | [13 empty] | 2.1870 | 2.1860 |  | 0.5000 X 0.2500 |  |  |  |  | Yes | Ambient Temp F=70 | Size=4412; Design=1904; Arrangement=3S; % Width=110.0; Discharge=CCW; Rotation=CCW; CFM=4000; SP=86.8; BHP=86.8; RPM=1180; Max Temp F=100; Effective Wheel Dia=48 15/16; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Wheel Material=CAST IRON; Hub=19-5-289; Coupling=FALK G20, SIZE 1025G, BORE 2 3/16 NOT INCL.; Blades=10; Shaft Dia=2 3/16; Brg Centers=40 1/8; Critical Speed RPM=1933; BX=33.88; STB=19.31; OH=9.38; STH=2.81; Bearing Size=2 3/16; Bearing Series=LINK BELT SERIES 300; Drive=Direct | Open
401902 | HDX | OK | pdf_vision | Quote Run.pdf |  |  | SN401902 | 4400 | 2300B |  |  | 9H | 100.0 | 100.0 PCT | CW | 44 | 13500 | 14.10 | 41.0 | 1665 | 480 | 662 | 0.0331 | 100.0 | 1665 | 19180 | 3 7/16 | 25 | 2585 | 54 7/16 | 13.66 | 15 7/16 | 13 5/16 | 142 | 1.94 | 3 7/16 BEARINGS | LINK BELT SERIES 6800 | 400000 | FLOAT | 636 | FIXED | 519 | 106 | 524 | 2068 | 1045 STEEL | 0.30 | 0.40 |  |  | ASTM A1011-HSLAS | 0.179 (7) | ASTM A1011-HSLAS | 0.179 (7) | ASTM A572 X-TEN | 5/16 |  |  |  | 11 | 2414 | 3380 | [5 empty] | 9.2 | 3.4 | 405 | Z |  | 1260 | 3/16 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 1.897 |  |  |  |  | 3926 | 52035 | HUB 23-5-424 BORE 3 3/16 CAST STEEL |  | Belt |  |  |  | Yes | Yes | [5 empty] | 3 3/16 | [10 empty] | Yes | Ambient Temp F=90 F | Size=4400; Design=2300B; Arrangement=9H; % Width=100.0; Discharge=100.0 PCT; Rotation=CW; CFM=13500; SP=14.10; BHP=41.0; RPM=1665; Max Temp F=662; Effective Wheel Dia=44; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 (7); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 (7); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=HUB 23-5-424 BORE 3 3/16 CAST STEEL; Blades=11; Shaft Dia=3 7/16; Brg Centers=25; Critical Speed RPM=2585; BX=15 7/16; STB=13 5/16; OH=13.66; STH=1.94; Bearing Size=3 7/16 BEARINGS; Bearing Series=LINK BELT SERIES 6800; Motor Frame=405; Motor Position=Z; Drive=Belt | Open
401913 | HD-PFD-IAF | OK | pdf_vision | QT RUNS.pdf |  |  | SN401913 | 4900 | 5800 |  |  | 4S | 100.0 | UB | CCW | 48 5/8 | 22000 | 28.00 | 147.9 | 1770 | 70 | 70 | 0.0750 | 150.0 | 1800 | 22914 | 2 7/16 | 16 | 3797 | 33 | 3/16 | 13 | 1/8 |  | 2.38 | 2 | 7/16 | 300 | FIXED | -41 | FIXED | 410 | 272 | 470 | 1879 | 1045 STEEL | 0.69 | 0.47 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 (7) |  |  |  | 10 | 2569 | [8 empty] | 445T | [12 empty] | 49-5-145-A BORE 2 3/16 | FALK G20, SIZE 1030G, BORE 2.438 | Direct |  |  |  | Yes | Yes | [5 empty] | 2 3/16 |  |  | 2.4370 | 2.4360 | 2.4375 | 0.6250 X 0.3125 | [5 empty] | Ambient Temp F=70; Coupling Ref=SKE-9-357 | Size=4900; Design=5800; Arrangement=4S; % Width=100.0; Discharge=UB; Rotation=CCW; CFM=22000; SP=28.00; BHP=147.9; RPM=1770; Max Temp F=70; Effective Wheel Dia=48 5/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 (7); Hub=49-5-145-A BORE 2 3/16; Coupling=FALK G20, SIZE 1030G, BORE 2.438; Blades=10; Shaft Dia=2 7/16; Brg Centers=16; Critical Speed RPM=3797; BX=13; STB=1/8; OH=3/16; STH=2.38; Bearing Size=2; Bearing Series=7/16; Motor Frame=445T; Drive=Direct | Open
402232 | GENERAL LINE | OK | generic_text | 402232 D64 Wheel Construction, 304L S.S..docx | [103 empty] | REF=64-5-0013-01-60 | REF=64-5-0013-01-60 | Open
402395 | HDX | OK | cbc_qt_run_text | Quote Run.txt |  |  | 402395 | 2700 | 1902 |  |  | 7S1 | 95.0 | TH | CW |  | 9029 | 3.75 | 8.5 | 1765 | 100 | 100 | 0.0710 | 10.0 | 1765 | 12476 | 1 7/16 | 33 | 2673 |  |  |  | 5.12 | 19 | 1.69 | 1 7/16 | LINK BELT SERIES 300 | 400000 | FLOAT | 85 | FIXED | 24 | 43 | 51 | 2138 | 1045 STEEL | 0.23 | 0.16 | 18 1/8 |  | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.060 (16) | ASTM A1011-HSLAS | 0.135 (10) |  |  |  | 10 | 2294 | 2870 | [7 empty] | 215T |  |  | 160 | 3/16 C.Q. HRS | SK-9-236 LOW PRESSURE, 36 IN. CENTERS | 3.870 |  | Included |  |  | 1640 | 36610 | 19-5-26 |  | Direct |  |  |  |  | Yes | [8 empty] | 1.4370 | 1.4360 |  | 0.3750 X 0.1875 | 48 1/2 | 10 3/8 | 3 |  | Yes | Ambient Temp F=90; Discharge Height (A)=30 3/4; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=30; Base Width (F)=40 3/4; Inlet Box Width (B)=48 1/2; Inlet Box Length To Cl (J)=34 3/4; Shaft Height (H)=25 1/4; Total Vert Height (TV)=60; Max Right of CL to Hsg (RH)=30; Max Left of CL to Disch (LH)=26 3/4; Span (S)=33 11/16; Inboard Brg Center To Cl (SL)=11 3/4; Outboard Brg Center To Cl (SR)=21 15/16; Drive End of Shaft to CL (K)=16 7/8; Outboard End Of Shaft To Cl (M)=23 11/16; Base Flange to CL (D)=36 9/16; Box Cl To Hsg Cl (P)=14 1/16; Box Width Os (C)=10 3/8 | Size=2700; Design=1902; Arrangement=7S1; % Width=95.0; Discharge=TH; Rotation=CW; CFM=9029; SP=3.75; BHP=8.5; RPM=1765; Max Temp F=100; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.060 (16); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.135 (10); Hub=19-5-26; Blades=10; Shaft Dia=1 7/16; Brg Centers=33; Critical Speed RPM=2673; STB=5.12; STH=1.69; Bearing Size=1 7/16; Bearing Series=LINK BELT SERIES 300; Housing Width (N)=18 1/8; Motor Frame=215T; Drive=Direct | Open
402395 | HDX | CHECK VISION | pdf_vision | QUOTE RUN.pdf |  |  | SN402395 | 2700 | 1902 |  |  | 781 | 95.0 | 0 | CW |  | 9029 | 3.75 | 8.5 | 1765 | 100 | 100 | 0.0710 | 10.0 | 1765 | 12476 | 7/16 | 33 11/16 | 2673 | 0.56 | 0.23 | 0.16 | 5.12 | 19 | 1.69 | 7/16 | 300 | 400000 | FLOAT | 85 | FIXED | 24 | 43 | 51 | 2138 | 1045 STEEL | 0.23 | 0.16 |  |  | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.060 (16) | ASTM A1011-HSLAS | 0.135 (10) |  |  | CAST IRON | 10 | 2294 | 2870 | [7 empty] | 215T |  |  | 160 | 3/16 C.Q. HRS | SK-9-236 LOW PRESSURE, 36 IN. CENTERS | 3.870 |  |  |  |  | 1640 | 36610 | 19-5-26 | REXNORD E SIZE E5 | BELT |  |  |  |  | Yes | [8 empty] | 1.4370 | 1.4360 |  | 0.3750 X 0.1875 | 48 1/2 | 10 3/8 | 3 |  | Yes | Ambient Temp F=90 | Size=2700; Design=1902; Arrangement=781; % Width=95.0; Discharge=0; Rotation=CW; CFM=9029; SP=3.75; BHP=8.5; RPM=1765; Max Temp F=100; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.060 (16); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.135 (10); Wheel Material=CAST IRON; Hub=19-5-26; Coupling=REXNORD E SIZE E5; Blades=10; Shaft Dia=7/16; Brg Centers=33 11/16; Critical Speed RPM=2673; BX=0.16; STB=5.12; OH=0.23; STH=1.69; Bearing Size=7/16; Bearing Series=300; Motor Frame=215T; Drive=BELT | Open
402467 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 402467 | 2412 | 1903 |  | PACKAGED FORCED DRAFT FAN | 8S | 100.0 | TAU | CCW | 25 3/4 | 5500 | 6.90 | 8.3 | 1745 | 100 | 100 | 0.0710 | 10.0 | 1800 | 12123 | 2 7/16 | 12 | 5488 | 29 13/16 | 9.60 | 14 13/16 | 6 13/16 | 40 | 1.62 | 2 7/16 | LINK BELT SERIES 300 | 400000 | FIXED | -33 | FIXED | 164 | 35 | 40 | 3600 | 1045 STEEL | 0.07 | 0.03 |  |  | ASTM A1011-HSLAS | 0.048 (18) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 10 | 3895 | 4870 | [7 empty] | 215T |  |  | 160 | 10 GA C.Q. HRS | SK-9-236 LOW PRESSURE, 36 IN. CENTERS | 3.274 |  |  |  | Included |  |  | 19-5-1056 | FALK T10 | Direct |  |  |  |  | Yes | [7 empty] | Q1 BUSHING 2 7/16 | [8 empty] | Yes | Ambient Temp F=90 | Size=2412; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=8S; % Width=100.0; Discharge=TAU; Rotation=CCW; CFM=5500; SP=6.90; BHP=8.3; RPM=1745; Max Temp F=100; Effective Wheel Dia=25 3/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.048 (18); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=19-5-1056; Coupling=FALK T10; Blades=10; Shaft Dia=2 7/16; Brg Centers=12; Critical Speed RPM=5488; BX=14 13/16; STB=6 13/16; OH=9.60; STH=1.62; Bearing Size=2 7/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=215T; Drive=Direct | Open
402547 | HDX | CHECK VISION | pdf_vision | QT Run (Pricing Only) (11).pdf |  |  | 365-21-2738 | 5200 | 2301B |  |  | 881 | 100.0 | 100.0 PCT | CCW | 52 1/2 | 30974 | 32.50 | 239.4 | 1780 | 180 | 210 | 0.0480 | 300.0 | 2000 | 27499 | 3 11/16 | 15 | 3120 | 38 1/16 | 11.23 | 11 15/16 | 10 |  | 2.25 | 3 11/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -549 | FLOAT | 1609 | 0 | 1967 LB-FT2 | 2000 | 1045 STEEL | 0.49 | 0.31 |  |  | ASTM A242 CORTEN | 1/4 | ASTM A242 CORTEN | 1/2 | ASTM A242 CORTEN | 5/16 | ASTM A242 CORTEN | 1/4 | CAST STEEL | 11 | 2080 | 6220 | [7 empty] | 449T |  | ODP |  | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 18 IN. CENTERS | [7 empty] | 23-5-425 BORE 3 7/16 | FALK T10, SIZE 1100T, BORE 3.438 | Direct |  | Required |  | Yes | [6 empty] | 3 7/16 | [6 empty] | 53 5/8 | 17 1/2 | 7 |  | Yes | Ambient Temp F=90 F; MTL=1045 STEEL; Wheel WR2 Weight=896; Blades Count=11 | Size=5200; Design=2301B; Arrangement=881; % Width=100.0; Discharge=100.0 PCT; Rotation=CCW; CFM=30974; SP=32.50; BHP=239.4; RPM=1780; Max Temp F=210; Effective Wheel Dia=52 1/2; Blade Material=ASTM A242 CORTEN; Blade Gauge=1/4; Sideplate Material=ASTM A242 CORTEN; Sideplate Gauge=1/2; Backplate Material=ASTM A242 CORTEN; Backplate Gauge=5/16; Liner Material=ASTM A242 CORTEN; Liner Gauge=1/4; Wheel Material=CAST STEEL; Hub=23-5-425 BORE 3 7/16; Coupling=FALK T10, SIZE 1100T, BORE 3.438; Blades=11; Shaft Dia=3 11/16; Brg Centers=15; Critical Speed RPM=3120; BX=11 15/16; STB=10; OH=11.23; STH=2.25; Bearing Size=3 11/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=449T; Motor Enclosure=ODP; Drive=Direct | Open
402566 | GENERAL LINE | OK | cbc_qt_run_text | 402566_304 SS QT RUN.pdf |  |  | 402566 | 245 | 51A | 1 |  | 3 |  |  |  |  | 20500 | 0.62 | 9.8 | 1570 |  |  |  |  | 1885 | 9865 | 2 7/16 | 51 | 2263 |  |  |  | 6.39 |  |  | 1 15/16 | LINK BELT SERIES 200 | 400000 | FIXED | -12 | FIXED | 80 | 0 | 45 | 1885 | A240 304 SS | 0.11 | 0.19 |  |  | ASTM A240 304L SS | 0.060 (16) | ASTM A240 304L SS | 0.105 (12) | [6 empty] | 2462 | 5440 | [5 empty] | 12.2 | [14 empty] | 4-5-145 |  | Belt |  |  | Yes | [20 empty] | Size=245; Design=51A; Arrangement=3; Class=1; CFM=20500; SP=0.62; BHP=9.8; RPM=1570; Blade Material=ASTM A240 304L SS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A240 304L SS; Sideplate Gauge=0.105 (12); Hub=4-5-145; Shaft Dia=2 7/16; Brg Centers=51; Critical Speed RPM=2263; STB=6.39; Bearing Size=1 15/16; Bearing Series=LINK BELT SERIES 200; Drive=Belt | Open
402625 | HDX | OK | pdf_vision | QT Run (5).pdf |  |  | 253-21-2337 | 6300 | 6105 |  |  | 3SL | 70.0 | BOX | CW | 66 1/8 | 96125 | 8.91 | 834.4 | 1625 | 95 | 140 | 0.0690 | 1000.0 | 1625 | 30956 | 6 1/4 | 86 9/16 | 2361 | 1 1/4 | 1.01 06 | 73.44 | 19.38 |  | 3.69 | 3 15/16 | 6800 | 400000 | FIXED | 1642 | FLOAT | 655 | 0 | 4967 | 1842 | 1045 STEEL | 0.24 | 0.87 |  |  | ASTM A6 XF-100 | 3/8 | ASTM A242 CORTEN | 1/2 | ASTM A242 CORTEN | 1/2 |  |  | CAST STEEL | 10 | 1842 | 3140 | [11 empty] | 1/2 C.Q. HRS | SK-9-236 HI PRESSURE, 18 IN. CENTERS | 19.336 | 66.000 |  |  |  | 16453 | 243252 | 19-5-218 | THOMAS 71 SIZE 712, BORE 3 15/16 NOT INCL. | Direct |  | Required |  | Yes | [13 empty] | 118 1/2 | 25 1/8 | 789 | SK-19-72 | Yes | Ambient Temp F=90; SL=30.88 | Size=6300; Design=6105; Arrangement=3SL; % Width=70.0; Discharge=BOX; Rotation=CW; CFM=96125; SP=8.91; BHP=834.4; RPM=1625; Max Temp F=140; Effective Wheel Dia=66 1/8; Blade Material=ASTM A6 XF-100; Blade Gauge=3/8; Sideplate Material=ASTM A242 CORTEN; Sideplate Gauge=1/2; Backplate Material=ASTM A242 CORTEN; Backplate Gauge=1/2; Wheel Material=CAST STEEL; Hub=19-5-218; Coupling=THOMAS 71 SIZE 712, BORE 3 15/16 NOT INCL.; Blades=10; Shaft Dia=6 1/4; Brg Centers=86 9/16; Critical Speed RPM=2361; BX=73.44; STB=19.38; OH=1.01 06; STH=3.69; Bearing Size=3 15/16; Bearing Series=6800; Drive=Direct | Open
402835 | HDX | OK | pdf_vision | QT RUN.pdf |  |  | SN 402835 | 6000 | 5500 | ARR 7SL,100.0 PCT |  | 7SL | 100.0 | ROT CW, BOX | CW | 62 1/2 | 60811 | 38.70 | 453.0 | 1780 | 152 | 180 | 0.0517 | 500.0 | 1800 | 29452 | 4 11/16 | 62 1/2 | 2905 | 75.81 | 50.19 | 14.85 | 9.75 | 22.56 | 2.38 | 3 7/16 | LINK BELT SERIES 6800 | 170755 | FIXED | 840 | FLOAT | 328 | 0 |  | 1948 |  | 0.27 | 0.62 |  |  | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  | CAST STEEL | 16 | 1948 | [8 empty] | 10 |  | ODP | 4250 |  | SK-9-236 HI PRESSURE, 18 IN. CENTERS | 9.421 |  | Included | 3.00 |  | 15718 | 189579 | 49-5-146-I BORE 4 11/16 | THOMAS 71 SIZE 512, BORE 3 7/16 | Direct |  |  |  | Yes | [6 empty] | 4 11/16 |  |  | 3.4370 | 3.4355 |  | 0.8750 X 0.4375 | 81 3/4 | 25 13/16 | 789 | SK-55-11 | Yes | Ambient Temp F=90 F; Coupling Ref=SKE-9-478 | Size=6000; Design=5500; Arrangement=7SL; % Width=100.0; Discharge=ROT CW, BOX; Rotation=CW; Class=ARR 7SL,100.0 PCT; CFM=60811; SP=38.70; BHP=453.0; RPM=1780; Max Temp F=180; Effective Wheel Dia=62 1/2; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Wheel Material=CAST STEEL; Hub=49-5-146-I BORE 4 11/16; Coupling=THOMAS 71 SIZE 512, BORE 3 7/16; Blades=16; Shaft Dia=4 11/16; Brg Centers=62 1/2; Critical Speed RPM=2905; BX=14.85; STB=9.75; OH=50.19; STH=2.38; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=10; Motor Enclosure=ODP; Drive=Direct | Open
402912 | GENERAL LINE | OK | cbc_qt_run_text | Quote Run.txt |  |  | 402912 | 135 | 51A | 1 |  | 3 |  |  |  |  | 2400 | 5.93 | 3.3 | 3500 |  |  |  |  | 5288 | 12112 | 15/16 | 14 | 6592 |  |  |  | 4.19 | 4 | 1.19 | 15/16 | LINK BELT SERIES 200 | 400000 | FIXED | 17 | FIXED | 5 | 0 | 2 | 5288 | 1045 STEEL | 0.14 | 0.14 |  |  | ASTM A1008 HSLAS | 0.048 (18) | ASTM A1011 CS | 0.048 (18) | ASTM A1011 CS | 0.075 (14) |  |  |  | 8 | 5288 | 15600 | [20 empty] | 4-5-34 | FALK G20 | Direct | Required | [9 empty] | 15/16 | [11 empty] | Ambient Temp F=70 | Size=135; Design=51A; Arrangement=3; Class=1; CFM=2400; SP=5.93; BHP=3.3; RPM=3500; Blade Material=ASTM A1008 HSLAS; Blade Gauge=0.048 (18); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.048 (18); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.075 (14); Hub=4-5-34; Coupling=FALK G20; Blades=8; Shaft Dia=15/16; Brg Centers=14; Critical Speed RPM=6592; STB=4.19; STH=1.19; Bearing Size=15/16; Bearing Series=LINK BELT SERIES 200; Drive=Direct | Open
403049 | HDX | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | SN403049 | 4900 | 1904 |  |  | 781 | 90.0 | TH | CCW | 53 7/8 | 52796 | 29.80 | 305.0 | 1780 | 142 | 180 | 0.0622 | 350.0 | 1800 | 25400 | 4 11/16 | 69 1/16 | 2671 | 81.88 | 14.57 | 25.25 | 9.38 |  | 2.94 | 3 3/16 | 6800 | 136156 | FIXED | 837 | FLOAT | 321 | 0 | 1790 | 1907 |  | 0.20 | 0.55 |  |  | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.179 (7) | ASTM A572 X-TEN | 1/2 |  |  |  | 10 | 1932 | [10 empty] | ODP | 4000 |  | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 12.597 |  | Included | 3.00 |  | 12529 | 126726 | CAST STEEL | FAIK T10, SIZE 1100T, BORE 3 3/16 | DRIVE-FIXED |  |  |  | Yes | [9 empty] | 3.1870 | 3.1855 |  | 0.7500 X 0.3750 | 88 1/4 | 18 3/4 | 789 | SK-19-72 | Yes | Ambient Temp F=90 | Size=4900; Design=1904; Arrangement=781; % Width=90.0; Discharge=TH; Rotation=CCW; CFM=52796; SP=29.80; BHP=305.0; RPM=1780; Max Temp F=180; Effective Wheel Dia=53 7/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 (7); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Hub=CAST STEEL; Coupling=FAIK T10, SIZE 1100T, BORE 3 3/16; Blades=10; Shaft Dia=4 11/16; Brg Centers=69 1/16; Critical Speed RPM=2671; BX=25.25; STB=9.38; OH=14.57; STH=2.94; Bearing Size=3 3/16; Bearing Series=6800; Motor Enclosure=ODP; Drive=DRIVE-FIXED | Open
403212 | HD-PFD-IAF | OK | cbc_qt_run_text | Quote Run-2-11-22.txt |  |  | 403212 | 3612 | 1903 |  |  | 4S | 80.0 | TH | CCW | 38 5/16 | 17588 | 14.75 | 49.8 | 1780 | 97 | 122 | 0.0662 | 50.0 | 1800 | 18060 | [8 empty] | 2.25 | [15 empty] | ASTM A240 304L SS | 0.060 (16) | ASTM A240 304L SS | 0.135 (10) | ASTM A240 304L SS | 1/4 |  |  |  | 10 | 2357 | 3110 | 229 | 173 | 248 | 4.24 | 6.13 |  |  | 326T |  |  | 610 | 3/16 A240 304L SS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 6.711 |  | Not included |  | Yes | 2075 | 39768 | 19-5-1042 |  | Motor mounted |  |  | Yes |  | Yes | [5 empty] | 2 1/8 | [12 empty] | Size=3612; Design=1903; Arrangement=4S; % Width=80.0; Discharge=TH; Rotation=CCW; CFM=17588; SP=14.75; BHP=49.8; RPM=1780; Max Temp F=122; Effective Wheel Dia=38 5/16; Blade Material=ASTM A240 304L SS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A240 304L SS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A240 304L SS; Backplate Gauge=1/4; Hub=19-5-1042; Blades=10; STH=2.25; Motor Frame=326T; Drive=Motor mounted | Open
403213 | HD-PFD-IAF | OK | cbc_qt_run_text | Quote Run-2-11-22.txt |  |  | 403213 | 3612 | 1903 |  |  | 4S | 80.0 | TH | CCW | 38 5/16 | 17588 | 14.75 | 49.8 | 1780 | 97 | 122 | 0.0662 | 50.0 | 1800 | 18060 | [8 empty] | 2.25 | [15 empty] | ASTM A240 304L SS | 0.060 (16) | ASTM A240 304L SS | 0.135 (10) | ASTM A240 304L SS | 1/4 |  |  |  | 10 | 2357 | 3110 | 229 | 173 | 248 | 4.24 | 6.13 |  |  | 326T |  |  | 610 | 3/16 A240 304L SS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 6.711 |  | Not included |  | Yes | 2075 | 39768 | 19-5-1042 |  | Motor mounted |  |  | Yes |  | Yes | [5 empty] | 2 1/8 | [12 empty] | Size=3612; Design=1903; Arrangement=4S; % Width=80.0; Discharge=TH; Rotation=CCW; CFM=17588; SP=14.75; BHP=49.8; RPM=1780; Max Temp F=122; Effective Wheel Dia=38 5/16; Blade Material=ASTM A240 304L SS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A240 304L SS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A240 304L SS; Backplate Gauge=1/4; Hub=19-5-1042; Blades=10; STH=2.25; Motor Frame=326T; Drive=Motor mounted | Open
403414 | GENERAL LINE | OK | cbc_qt_run_text | 344-22-455 quote run.txt |  |  | 403414 | 40 | A10 |  |  | 4S | 85.0 | TH | CW |  | 10000 | 10.00 | 100.0 | 1800 | 70 | 70 | 0.0750 | 100.0 | 1800 | 20466 | [8 empty] | 3.44 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011 CS | 0.179 ( 7) |  |  |  | 12 | 2391 | 3750 | 247 | 292 | 388 | 6.86 | 7.32 |  |  | 445T |  |  | 1785 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 9.165 |  | Not included |  |  | 3826 | 29187 | 19-5-16 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 3 3/8 | [11 empty] | Ambient Temp F=90 | Size=40; Design=A10; Arrangement=4S; % Width=85.0; Discharge=TH; Rotation=CW; CFM=10000; SP=10.00; BHP=100.0; RPM=1800; Max Temp F=70; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.179 ( 7); Hub=19-5-16; Blades=12; STH=3.44; Motor Frame=445T; Drive=Motor mounted | Open
403458 | GENERAL LINE | OK | cbc_qt_run_text | UPDATED QT RUN.txt |  |  | 403458 | 445 | 51A | 1 |  | 9 |  |  |  |  | 26485 | 7.22 | 37.3 | 1200 |  |  |  |  | 1812 | 13646 | 2 15/16 | 8 | 6032 | 28 9/16 | 10.69 | 20 5/8 | 8 1/2 |  | 3.44 | 2 15/16 | LINK BELT SERIES 200 | 68619 | FIXED | 623 | FIXED | 217 | 0 | 167 | 1812 | A240 316 SS | 0.33 | 0.45 |  |  | ALUM 5052-H32 | 0.125 | ALUM 3003-O | 0.125 | ALUM 5052-H32 | 0.190 |  |  |  | 8 | 1891 | 3660 | [5 empty] | 17.3 | 8.9 | 365 | Z | ODP | 920 | [9 empty] | 4-5-121 |  | Belt | Required |  |  |  | Yes | [17 empty] | Ambient Temp F=90 | Size=445; Design=51A; Arrangement=9; Class=1; CFM=26485; SP=7.22; BHP=37.3; RPM=1200; Blade Material=ALUM 5052-H32; Blade Gauge=0.125; Sideplate Material=ALUM 3003-O; Sideplate Gauge=0.125; Backplate Material=ALUM 5052-H32; Backplate Gauge=0.190; Hub=4-5-121; Blades=8; Shaft Dia=2 15/16; Brg Centers=8; Critical Speed RPM=6032; BX=20 5/8; STB=8 1/2; OH=10.69; STH=3.44; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 200; Motor Frame=365; Motor Position=Z; Motor Enclosure=ODP; Drive=Belt | Open
403471 | HD-PFD-IAF | OK | pdf_vision | QT RUN.pdf |  |  | SN403471 | 4900 | 5500 | ARR 8S |  | 8S | 100.0 | DISCH BAU, ROT CW | CW | 46 7/8 | 24115 | 23.00 | 110.5 | 1780 | 300 | 300 | 0.0550 | 125.00 | 1800 | 22089 | 2 15/16 | 16 | 3535 | 38 5/16 | 10.70 | 17 1/8 | 8 7/8 |  | 2.00 | 2 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -87 | FLOAT | 484 | 0 | 454 | 1963 | 1045 STEEL | 0.40 | 0.26 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  | CAST STEEL |  | 2349 | [8 empty] | 444T |  | TEFC | 1893 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 6.293 |  | Included | 3.00 | Included | 1658 | 21627 | 49-5-145-G BORE 2 11/16 | FALK T10, SIZE 1100T, BORE 2.938 | Direct |  |  |  | Yes | Yes | [5 empty] | 2 11/16 |  |  | 2.9370 | 2.9355 | 2.9375 | 0.7500 X 0.3750 |  |  |  |  | Yes | Ambient Temp F=90; Coupling Ref=SKE-9-356 | Size=4900; Design=5500; Arrangement=8S; % Width=100.0; Discharge=DISCH BAU, ROT CW; Rotation=CW; Class=ARR 8S; CFM=24115; SP=23.00; BHP=110.5; RPM=1780; Max Temp F=300; Effective Wheel Dia=46 7/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Wheel Material=CAST STEEL; Hub=49-5-145-G BORE 2 11/16; Coupling=FALK T10, SIZE 1100T, BORE 2.938; Shaft Dia=2 15/16; Brg Centers=16; Critical Speed RPM=3535; BX=17 1/8; STB=8 7/8; OH=10.70; STH=2.00; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=444T; Motor Enclosure=TEFC; Drive=Direct | Open
403736 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 403736 | 402 | 51A | 3 |  | 4 |  |  |  |  | 28151 | 9.54 | 63.3 | 1800 | [5 empty] | 18555 | [8 empty] | 3.44 | [15 empty] | ASTM A1008 HSLAS | 0.060 (16) | ASTM A1011 CS | 0.075 (14) | ASTM A1011 CS | 0.179 ( 7) |  |  |  | 8 | 1994 | 4970 | 153 | 218 | 201 | 6.49 | 7.07 |  |  | 365T |  | TEFC | 1150 | [9 empty] | 4-5-39 |  | Motor mounted | Required |  |  |  | Yes | [5 empty] | 2 3/8 | [11 empty] | Ambient Temp F=85 | Size=402; Design=51A; Arrangement=4; Class=3; CFM=28151; SP=9.54; BHP=63.3; RPM=1800; Blade Material=ASTM A1008 HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.075 (14); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.179 ( 7); Hub=4-5-39; Blades=8; STH=3.44; Motor Frame=365T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
403763 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN REVISED WITH NEW BRGS (P300).txt |  |  | 403763 | 23.000 | 2302B |  |  | 1S | 100.0 | TH | CW | 23 7/16 | 4400 | 66.00 | 62.2 | 4374 | 70 | 70 | 0.0750 | 75.0 | 4374 | 26864 | 1 15/16 | 10 | 6959 | 23 3/4 | 5.38 | 6 5/16 | 7 |  | 0.98 | 1 15/16 | LINK BELT SERIES 300 | 119004 | FIXED | -7 | FLOAT | 138 | 0 | 35 | 5000 | 1045 STEEL | 0.32 | 0.19 |  |  | ASTM A1011 CS | 0.179 ( 7) | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 11 | 5043 | 12810 | [11 empty] | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 18 IN. CENTERS | 0.553 | [6 empty] | 23-5-423 | FALK T10 | Direct |  | Required |  | Yes | Yes | [5 empty] | 1 11/16 | [10 empty] | Yes | Ambient Temp F=90 | Size=23.000; Design=2302B; Arrangement=1S; % Width=100.0; Discharge=TH; Rotation=CW; CFM=4400; SP=66.00; BHP=62.2; RPM=4374; Max Temp F=70; Effective Wheel Dia=23 7/16; Blade Material=ASTM A1011 CS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 ( 7); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=23-5-423; Coupling=FALK T10; Blades=11; Shaft Dia=1 15/16; Brg Centers=10; Critical Speed RPM=6959; BX=6 5/16; STB=7; OH=5.38; STH=0.98; Bearing Size=1 15/16; Bearing Series=LINK BELT SERIES 300; Drive=Direct | Open
404016 | GENERAL LINE | OK | pdf_vision | Quote Run 404016.pdf |  |  | 404016 | 22.250 | 6100 |  |  | 4S | 65.0 | UB | CW | 22 1/4 | 8000 | 14.15 | 25.1 | 3500 | 70 | 70 | 0.0706 | 25.1 | 3600 | 20970 | 1 1/8 | 21 | [6 empty] | 1.62 | 1055 | [14 empty] | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.060 (16) | ASTM A1011-HSLAS | 0.075 (14) |  |  | C. IRON | 10 | 3740 | 5380 | 41 | 88 | 14 | 2.62 | 4.62 |  |  | 284TS |  | TEFC | 443 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 2.379 |  | Not included |  | Yes |  |  | 19-5-1055, Q2 BUSHING 1 5/8, C. IRON |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q2 BUSHING 1 5/8 | [9 empty] | Ambient Temp F=70; Outlet N x A=13 1/2 IN. X 25 3/8 IN. | Size=22.250; Design=6100; Arrangement=4S; % Width=65.0; Discharge=UB; Rotation=CW; CFM=8000; SP=14.15; BHP=25.1; RPM=3500; Max Temp F=70; Effective Wheel Dia=22 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.060 (16); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.075 (14); Wheel Material=C. IRON; Hub=19-5-1055, Q2 BUSHING 1 5/8, C. IRON; Blades=10; Shaft Dia=1 1/8; Brg Centers=21; STH=1.62; Bearing Size=1055; Motor Frame=284TS; Motor Enclosure=TEFC; Drive=Motor mounted | Open
404085 | HD-PFD-IAF | OK | pdf_vision | QT RUN-404085.pdf |  |  | SN404085 | 2412 | 1903 |  | PACKAGED FORCED DRAFT FAN | 8S | 100.0 | PCT | DISCH BH, ROT CW | 25 3/4 | 7650 | 21.00 | 32.6 | 3500 | 350 | 350 | 0.0490 | 40.0 | 3600 | 24245 | 2 3/16 | 12 | 4842 | 29 1/16 | 8.90 | 14 1/8 | 6 3/4 | 31 | 1.62 | 2 3/16 | LINK BELT SERIES 300 | 400000 | FIXED | -31 | FIXED | 155 | 140 | 40 | 3650 |  | 0.14 | 0.10 |  |  | ASTM A1011-HSLAS | 0.048 (18) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.179 (7) |  |  | 10 BLADES | 10 | 3862 | 4830 | [7 empty] | 324TS |  |  | 550 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 3.274 |  |  |  | Included |  |  | 19-5-1056, Q1 BUSHING 2 3/16, C. IRON | FALK T10, SIZE 1070T, BORE 2.188 | Direct |  |  |  |  | Yes | [7 empty] | Q1 BUSHING 2 3/16 | [8 empty] | Yes | Ambient Temp F=90 | Size=2412; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=8S; % Width=100.0; Discharge=PCT; Rotation=DISCH BH, ROT CW; CFM=7650; SP=21.00; BHP=32.6; RPM=3500; Max Temp F=350; Effective Wheel Dia=25 3/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.048 (18); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 (7); Wheel Material=10 BLADES; Hub=19-5-1056, Q1 BUSHING 2 3/16, C. IRON; Coupling=FALK T10, SIZE 1070T, BORE 2.188; Blades=10; Shaft Dia=2 3/16; Brg Centers=12; Critical Speed RPM=4842; BX=14 1/8; STB=6 3/4; OH=8.90; STH=1.62; Bearing Size=2 3/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=324TS; Drive=Direct | Open
404135 | HDX | CHECK VISION | pdf_vision | QT RUN-REV FEA.pdf |  |  | SN404135 | 3300 | 1911 |  |  | 85 | 85.0 | CLEAR FD FAN | CW | 35 9/16 | 20033 | 14.43 | 55.1 | 1954 | 97 | 150 | 0.0702 | 60.0 | 1954 | 18192 | 2 11/16 | 14 | 4197 | 32 9/16 | 9.46 | 6 | 7 1/8 | MI.5 | 3.19 | 2 11/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -92 | FLOAT | 376 | 0 | 198 | 2403 | 1045 STEEL | 0.25 | 0.14 |  |  | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A572 X-TEN | 1/4 |  |  | CAST STEEL | 8 | 2403 | 4590 | [7 empty] | 364T |  |  | 835 |  | SK-9-236 MED PRESSURE, 24 IN. CENTERS |  |  |  |  | Included |  |  | 19-5-11 | THOMAS 71 SIZE 350, BORE 2.688 | 3030 |  |  |  | Yes | Yes | [5 empty] | 2 7/16 |  |  | 2.6870 | 2.6860 | 2.6875 | 0.6250 X 0.3125 |  |  |  |  | Yes | Ambient Temp F=90 F | Size=3300; Design=1911; Arrangement=85; % Width=85.0; Discharge=CLEAR FD FAN; Rotation=CW; CFM=20033; SP=14.43; BHP=55.1; RPM=1954; Max Temp F=150; Effective Wheel Dia=35 9/16; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Wheel Material=CAST STEEL; Hub=19-5-11; Coupling=THOMAS 71 SIZE 350, BORE 2.688; Blades=8; Shaft Dia=2 11/16; Brg Centers=14; Critical Speed RPM=4197; BX=6; STB=7 1/8; OH=9.46; STH=3.19; Bearing Size=2 11/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=364T; Drive=3030 | Open
404173 | GENERAL LINE | OK | pdf_vision | QT RUN-FEA.pdf |  |  | SN404173 | 4900 | 95 |  |  | 4S | 100.0 | UB | CW | 46 9/16 | 50000 | 22.00 | 216.4 | 1772 | 70 | 70 | 0.0737 |  | 1800 | 24130 | [8 empty] | 2.94 | [15 empty] | ASTM A6 XF-100 | 3/8 | ASTM A6 XF-100 | 1/4 | ASTM A6 XF-100 | 5/16 |  |  | 2204 | 10 |  | 2760 | 608 | 432 | 1378 | 7.16 | 7.32 |  |  | 449T |  | TEFC | 3250 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 13.033 |  | Not included |  | Yes | 7531 | 83596 | 19-5-212 |  | Motor mounted |  |  | Yes |  | Yes | [5 empty] | 3 3/8 | [9 empty] | SK-19-72 |  | Ambient Temp F=90; Max SP=250.0; Hub Material=CAST STEEL; Hub Gauge=3/8; Number of Blades=10; Wheel Weight=608; WR2 Weight=1378; Wheel Thrust=432; WR2 Thrust=1378 | Size=4900; Design=95; Arrangement=4S; % Width=100.0; Discharge=UB; Rotation=CW; CFM=50000; SP=22.00; BHP=216.4; RPM=1772; Max Temp F=70; Effective Wheel Dia=46 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=3/8; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=1/4; Backplate Material=ASTM A6 XF-100; Backplate Gauge=5/16; Wheel Material=2204; Hub=19-5-212; Blades=10; STH=2.94; Motor Frame=449T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
404188 | GENERAL LINE | OK | d64_wheel_construction | 404188_339-21-1559 D64 Wheel Construction (Inner Ring).xlsx | [103 empty] | Fan Size=165; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=50000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.1345 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=165; Outer Ring Thickness=0.1345; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=50000 | Open
404216 | HDX | CHECK VISION | pdf_vision | QT Run.pdf |  |  | SN404216 | 6000 | 2308B |  |  | 781 | 50.0 | TH | CW | 64 13/16 | 24000 | 38.00 | 233.1 | 1480 | 170 | 201 | 0.0530 | 250.0 | 1500 | 25447 | 5 1/4 | 51 1/2 | 3666 | 5 1/4 | 63.69 | 40.12 | 8.62 | 15.75 | 14.85 | 3 7/16 | LINK BELT SERIES 6800 | 140846 | FIXED | 1058 | FLOAT | 484 | 0 | 3971 | 1852 | 1045 STEEL | 0.15 | 0.38 |  |  | ASTM CQ HRS A36 | 1/4 | ASTM A572 X-TEN | 3/8 | ASTM A572 X-TEN | 1/2 | CAST STEEL | 1/4 | THICK (GA) | 11 | 1852 | 12370 | [7 empty] | 449T |  | ODP | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 19 IN. CENTERS | 2.473 | [6 empty] | 5.2500 | FALK G20, SIZE 1030G, BORE 3 7/16 | Direct |  |  |  | Yes | Yes | [5 empty] | 5 1/4 |  |  | 3.4370 | 3.4355 |  | 0.8750 X 0.4375 | 62 |  | 1 |  | Yes | Ambient Temp F=90 | Size=6000; Design=2308B; Arrangement=781; % Width=50.0; Discharge=TH; Rotation=CW; CFM=24000; SP=38.00; BHP=233.1; RPM=1480; Max Temp F=201; Effective Wheel Dia=64 13/16; Blade Material=ASTM CQ HRS A36; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=3/8; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Liner Material=CAST STEEL; Liner Gauge=1/4; Wheel Material=THICK (GA); Hub=5.2500; Coupling=FALK G20, SIZE 1030G, BORE 3 7/16; Blades=11; Shaft Dia=5 1/4; Brg Centers=51 1/2; Critical Speed RPM=3666; BX=40.12; STB=8.62; OH=63.69; STH=14.85; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=449T; Motor Enclosure=ODP; Drive=Direct | Open
404232 | GENERAL LINE | OK | d64_wheel_construction | 404232_311-20-2377 D64 Wheel Construction (Inner Ring).xlsx | [103 empty] | Fan Size=245; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=80000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.25 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=245; Outer Ring Thickness=0.25; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=80000 | Open
404318 | GENERAL LINE | OK | pdf_vision | Quote Run.pdf |  |  | 404318 | 2412 | 6105 |  |  | 4S | 50.0 | PCT | CCW | 25 3/4 | 7000 | 28.00 | 42.0 | 3500 | 70 | 105 | 0.0750 | 50.0 | 3600 | 24245 | 1 5/8 | 20 | [6 empty] | 1.62 |  | SK-9-105 | [13 empty] | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.105 (12) |  |  | Q2 BUSHING 1 7/8, C. IRON | 10 | 3764 | 6930 | 61 | 155 | 28 | 2.60 | 4.12 |  |  | 326TS |  | TEFC |  | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 2.692 |  | Not included |  | Yes |  |  | 19-5-1056 |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q2 BUSHING 1 7/8 | [7 empty] | SK-19-72 |  | Ambient Temp F=70; Ambient Temp=70; Wheel Weight=61; Thrust=155; Motor=326TS FR MOTOR; Housing=7 GA C.Q. HRS; Inlet Vane Control=2 1/4 CENTER, TORQUE 351 IN-LB | Size=2412; Design=6105; Arrangement=4S; % Width=50.0; Discharge=PCT; Rotation=CCW; CFM=7000; SP=28.00; BHP=42.0; RPM=3500; Max Temp F=105; Effective Wheel Dia=25 3/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.105 (12); Wheel Material=Q2 BUSHING 1 7/8, C. IRON; Hub=19-5-1056; Blades=10; Shaft Dia=1 5/8; Brg Centers=20; STH=1.62; Bearing Series=SK-9-105; Motor Frame=326TS; Motor Enclosure=TEFC; Drive=Motor mounted | Open
404346 | GENERAL LINE | CHECK VISION | pdf_vision | Quote Run 404346.pdf |  |  | 404346 | 4900 | 6195 | 4S |  | 4S | 90.0 | DISCH BAU | ROT CW | 46 9/16 | 21900 | 22.00 | 198.5 | 1770 | 70 | 70 | 0.0750 | 200.0 | 1800 | 21936 | [8 empty] | 2.94 | [15 empty] | ASTM A6 XF-100 | 3/16 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  | CAST IRON | 10 | 2010 | 2840 | 493 | 432 | 1068 | 6.44 | 7.32 |  |  | 447T |  | TEFC | 2850 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 12.597 |  | Not included |  | Included | 6848 | 49431 | 19-5-289 BORE 3 3/8 | 6195 | Motor mounted |  |  | Yes |  | Yes | [5 empty] | 3 3/8 | [9 empty] | SK-19-72 |  | Ambient Temp F=70 | Size=4900; Design=6195; Arrangement=4S; % Width=90.0; Discharge=DISCH BAU; Rotation=ROT CW; Class=4S; CFM=21900; SP=22.00; BHP=198.5; RPM=1770; Max Temp F=70; Effective Wheel Dia=46 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Wheel Material=CAST IRON; Hub=19-5-289 BORE 3 3/8; Coupling=6195; Blades=10; STH=2.94; Motor Frame=447T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
404357 | HDX | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | SN404357 | 5414 | 5500 |  |  | 781 | 100.0 | 100.0 PCT | CCW | 53 1/4 | 1793 | 29.70 | 211.2 | 1780 | 149 | 180 | 0.0540 | 250.0 | 1800 | 25094 | 3 11/16 | 55 7/8 | 2976 |  |  |  | 9.00 |  | 2.19 | 2 11/16 | 6800 |  | FIXED | 475 | FLOAT | 172 | 0 | 919 | 2125 | 1045 STEEL | 0.27 | 0.65 |  |  | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A570 X-TEN | 5/16 |  |  | CAST STEEL | 16 | 2205 | [10 empty] | ODP | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 7.701 |  | Included | 3.00 |  | 9363 | 99141 | 23-5-424 | FALK T10, SIZE 1100T | DRIVE-FIXED |  |  |  | Yes | Yes | [8 empty] | 2.6870 | 2.6860 |  | 0.6250 X 0.3125 | 74 | 23 5/16 | 789 | SK-55-11 | Yes | Ambient Temp F=90 F; Coupling Ref=SKE-9-356 | Size=5414; Design=5500; Arrangement=781; % Width=100.0; Discharge=100.0 PCT; Rotation=CCW; CFM=1793; SP=29.70; BHP=211.2; RPM=1780; Max Temp F=180; Effective Wheel Dia=53 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A570 X-TEN; Backplate Gauge=5/16; Wheel Material=CAST STEEL; Hub=23-5-424; Coupling=FALK T10, SIZE 1100T; Blades=16; Shaft Dia=3 11/16; Brg Centers=55 7/8; Critical Speed RPM=2976; STB=9.00; STH=2.19; Bearing Size=2 11/16; Bearing Series=6800; Motor Enclosure=ODP; Drive=DRIVE-FIXED | Open
404438 | GENERAL LINE | OK | d64_wheel_construction | 404438_339-22-229 D64 Wheel Construction (Inner Ring).xlsx | [103 empty] | Fan Size=182; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=50000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.25 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=182; Outer Ring Thickness=0.25; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=50000 | Open
404457 | GENERAL LINE | OK | cbc_qt_run_text | Preliminary QT Run.txt |  |  | 404457 | 6000 | 6195 |  |  | 8S | 90.0 | UB | CW | 57 | 57322 | 12.66 | 146.1 | 1186 | 104 | 130 | 0.0684 | 150.0 | 1200 | 19698 | 3 7/16 | 20 | 2125 | 42 7/16 | 12.33 | 24 7/16 | 8 3/8 | 112 | 4.12 | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -514 | FLOAT | 1614 | 0 | 3154 | 1700 | 1045 STEEL | 0.44 | 0.27 | 39 3/4 |  | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/2 |  |  |  | 10 | 1736 | 2870 | [7 empty] | 447T |  |  | 2850 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 18.840 |  |  |  | Included | 11279 | 106707 | 19-5-17 |  | Direct |  |  | Yes |  | Yes | [5 empty] | 3 7/16 |  |  | 3.4370 | 3.4355 | 3.4375 | 0.8750 X 0.4375 |  |  |  | SK-19-72 | Yes | Ambient Temp F=14; Discharge Height (A)=68 1/4; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=3; Discharge Flange to CL (E)=42 1/2; Base Width (F)=79 1/2; Shaft Height (H)=67 1/4; Total Vert Height (TV)=109 3/4; Max Right of CL to Hsg (RH)=48 3/4; Max Left of CL to Disch (LH)=71 1/4; Base Flange to CL (D)=99 9/16; Drive End of Shaft to CL (K)=52 13/16; Mtg Flange to CL (LR)=22 1/8 | Size=6000; Design=6195; Arrangement=8S; % Width=90.0; Discharge=UB; Rotation=CW; CFM=57322; SP=12.66; BHP=146.1; RPM=1186; Max Temp F=130; Effective Wheel Dia=57; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Hub=19-5-17; Blades=10; Shaft Dia=3 7/16; Brg Centers=20; Critical Speed RPM=2125; BX=24 7/16; STB=8 3/8; OH=12.33; STH=4.12; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=39 3/4; Motor Frame=447T; Drive=Direct | Open
404459 | HDX | CHECK VISION | pdf_vision | QT RUN REV A.pdf |  |  | SN404459 | 8478 | 1904 |  |  | 781 | 100.0 | PCT | DISCH BAU, ROT CCW | 93 3/8 | 139922 | 22.00 | 848.5 | 1180 | 90 | 550 | 0.0357 | 900.0 | 1200 | 29331 | 9 | 118 1/8 | 1775 | 7 1/4 |  |  | 12.50 |  |  | 4 15/16 | LINK BELT SERIES 6800 | 274120 | FIXED | 4839 | FLOAT | 1891 | 0 | 35680 | 1209 | 1045 STEEL | 0.24 | 0.58 |  |  | ASTM A1011-HSLAS | 0.179 (7) | ASTM A572 X-TEN | 1/8 | ASTM A572 X-TEN | 1 |  |  | CAST STEEL | 10 | 1209 | 1610 | [7 empty] | 10 |  |  | 9200 | 3/8 C.Q. HRS | SK-9-236 HI PRESSURE, 19 IN. CENTERS | 39.145 | 93.500 | Included | 3.000 |  |  |  | 19-5-1640 | THOMAS 71-8 SIZE 712 | Direct |  |  | Yes | Yes | [9 empty] | 4.9370 | 4.9355 |  | 1.2500 X 0.6250 | 168 1/4 | 35 3/8 | 1177 |  | Yes | Ambient Temp F=90 | Size=8478; Design=1904; Arrangement=781; % Width=100.0; Discharge=PCT; Rotation=DISCH BAU, ROT CCW; CFM=139922; SP=22.00; BHP=848.5; RPM=1180; Max Temp F=550; Effective Wheel Dia=93 3/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 (7); Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/8; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1; Wheel Material=CAST STEEL; Hub=19-5-1640; Coupling=THOMAS 71-8 SIZE 712; Blades=10; Shaft Dia=9; Brg Centers=118 1/8; Critical Speed RPM=1775; STB=12.50; Bearing Size=4 15/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=10; Drive=Direct | Open
404460 | HD-PFD-IAF | OK | pdf_vision | 4044640-QT RUN.pdf |  |  | SN404460 | 2412 | 1903 |  | PACKAGED FORCED DRAFT FAN | 4S1 | 85.0 | DB | CW | 25 3/4 | 9549 | 14.68 | 31.2 | 2960 | 103 | 133 | 0.0655 | 40.0 | 3000 | 20204 | [8 empty] | 1.62 | [15 empty] | ASTM A1011-HSLAS | 0.048 (18) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 10 | 3967 | 4960 | 77 | 97 | 38 | 2.96 | 4.12 |  |  | 286T |  | ODP | 390 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 3.104 |  | Not included |  |  |  |  | 19-5-1056, Q1 BUSHING 1 7/8 , C. IRON |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q1 BUSHING 1 7/8 |  |  |  |  | 44 | 9 5/16 | 10 |  |  | Ambient Temp F=90; Wheel Weight=77; Thrust=97; Motor=286T FR MOTOR; Outlet N X A=16 IN. X 27 15/16 IN.; Box B X C=44 IN. X 9 5/16 IN.; Base=202 | Size=2412; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S1; % Width=85.0; Discharge=DB; Rotation=CW; CFM=9549; SP=14.68; BHP=31.2; RPM=2960; Max Temp F=133; Effective Wheel Dia=25 3/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.048 (18); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=19-5-1056, Q1 BUSHING 1 7/8 , C. IRON; Blades=10; STH=1.62; Motor Frame=286T; Motor Enclosure=ODP; Drive=Motor mounted | Open
404503 | GENERAL LINE | OK | cbc_qt_run_text | 404503_QT Run.txt |  |  | 404503 | 33 | A10 |  |  | 4S | 65.0 | BAU | CCW |  | 13310 | 7.50 | 18.3 | 1475 | 100 | 100 | 0.0650 | 22.0 | 1500 | 13983 | [8 empty] | 3.19 | [15 empty] | ASTM A240 316L SS | 0.060 (16) | ASTM A240 316L SS | 0.105 (12) | ASTM A240 316L SS | 0.135 (10) |  |  |  | 12 | 2782 | 4160 | 158 | 91 | 139 | 5.45 | 7.07 |  |  | 284T |  | ODP | 355 | 10 GA C.Q. HRS | SK-9-236 MED PRESSURE, 30 IN. CENTERS | 5.812 |  | Not included |  |  |  |  | 19-5-16 |  | Motor mounted | Required |  | Yes |  | Yes | [5 empty] | 1 7/8 | [11 empty] | Ambient Temp F=70 | Size=33; Design=A10; Arrangement=4S; % Width=65.0; Discharge=BAU; Rotation=CCW; CFM=13310; SP=7.50; BHP=18.3; RPM=1475; Max Temp F=100; Blade Material=ASTM A240 316L SS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A240 316L SS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A240 316L SS; Backplate Gauge=0.135 (10); Hub=19-5-16; Blades=12; STH=3.19; Motor Frame=284T; Motor Enclosure=ODP; Drive=Motor mounted | Open
404504 | GENERAL LINE | OK | cbc_qt_run_text | 404504_QT Run.txt |  |  | 404504 | 33 | A10 |  |  | 4S | 65.0 | BAU | CCW |  | 13310 | 7.50 | 18.3 | 1475 | 100 | 100 | 0.0650 | 22.0 | 1500 | 13983 | [8 empty] | 3.19 | [15 empty] | ASTM A240 316L SS | 0.060 (16) | ASTM A240 316L SS | 0.105 (12) | ASTM A240 316L SS | 0.135 (10) |  |  |  | 12 | 2782 | 4160 | 158 | 91 | 139 | 5.45 | 7.07 |  |  | 284T |  | ODP | 355 | 10 GA C.Q. HRS | SK-9-236 MED PRESSURE, 30 IN. CENTERS | 5.812 |  | Not included |  |  |  |  | 19-5-16 |  | Motor mounted | Required |  | Yes |  | Yes | [5 empty] | 1 7/8 | [11 empty] | Ambient Temp F=70 | Size=33; Design=A10; Arrangement=4S; % Width=65.0; Discharge=BAU; Rotation=CCW; CFM=13310; SP=7.50; BHP=18.3; RPM=1475; Max Temp F=100; Blade Material=ASTM A240 316L SS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A240 316L SS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A240 316L SS; Backplate Gauge=0.135 (10); Hub=19-5-16; Blades=12; STH=3.19; Motor Frame=284T; Motor Enclosure=ODP; Drive=Motor mounted | Open
404508 | HDX | OK | pdf_vision | QT RUN.pdf |  |  | SN 404508 | 3612 | 1903 |  |  | 7S | 70.0 | TAU | CW | 38 5/16 | 8710 | 7.00 | 11.9 | 1170 | 115 | 115 | 0.0652 | 15.0 | 1200 | 12040 | 2 11/16 | 36 3/16 | 3408 |  |  |  | 9.95 |  | 2.25 | 1 11/16 |  |  | FIXED | 165 | FLOAT | 75 | 0 |  | 1960 |  | 0.10 | 0.22 |  |  | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.179 (7) |  |  | CAST IRON | 10 | 1959 | 2450 | [7 empty] | 284T |  |  | 355 | 3/16 C.Q. RHS | SK-9-236 LOW PRESSURE, 36 IN. CENTERS | 6.458 |  |  |  | Yes | 2587 | 81650 | 19-5-16 |  | Direct |  |  |  | Yes | [9 empty] | 1.6870 | 1.6860 | 1.6875 | 0.3750 X 0.1875 |  |  |  |  | Yes | Ambient Temp F=90 | Size=3612; Design=1903; Arrangement=7S; % Width=70.0; Discharge=TAU; Rotation=CW; CFM=8710; SP=7.00; BHP=11.9; RPM=1170; Max Temp F=115; Effective Wheel Dia=38 5/16; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.075 (14); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 (7); Wheel Material=CAST IRON; Hub=19-5-16; Blades=10; Shaft Dia=2 11/16; Brg Centers=36 3/16; Critical Speed RPM=3408; STB=9.95; STH=2.25; Bearing Size=1 11/16; Motor Frame=284T; Drive=Direct | Open
404641 | GENERAL LINE | CHECK VISION | pdf_vision | Quote Run 404641.pdf |  |  | 404641 | 5414 | 6195 |  |  | 4S | 90.0 | UB | CW | 51 9/16 | 15,080 | 15.00 | 294.6 | 1770 | 70 | 70 | 0.0733 | 300.0 | 1800 | 26715 |  | 19-5-12 | [6 empty] | 3.38 | [15 empty] | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 5/16 | ASTM A572 X-TEN | 3/8 |  |  | CAST STEEL | 10 | 2086 | 2790 | 773 | 649 | 1988 | 7.46 | 8.26 |  |  | 449T |  | TEFC | 3250 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 15.384 |  | Not included |  | Included | 8154 | 73727 | BORE 3 3/8 |  | Motor mounted |  |  | Yes | [7 empty] | 3 3/8 | [9 empty] | SK-19-72 |  | Ambient Temp F=70; Blade Weight=531; Sideplate Weight=627; Backplate Weight=786; Hub Weight=44; Wheel Weight=773; Blades Count=10; Resonance CPM=2790; Wheel Weight Total=773; Thrust=649; WR2=1988 LB-FT2; Outlet=35 7/8 IN. X 61 3/4 IN.; Motor Weight=3250; Housing Weight=2607; Total Weight=8154; Price=73727 | Size=5414; Design=6195; Arrangement=4S; % Width=90.0; Discharge=UB; Rotation=CW; CFM=15,080; SP=15.00; BHP=294.6; RPM=1770; Max Temp F=70; Effective Wheel Dia=51 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=5/16; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Wheel Material=CAST STEEL; Hub=BORE 3 3/8; Blades=10; Brg Centers=19-5-12; STH=3.38; Motor Frame=449T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
404653 | GENERAL LINE | OK | cbc_qt_run_text | Quote Run Updated.txt |  |  | 404653 | 3612 | 6195 |  |  | 9H1 | 100.0 | UB | CW | 34 11/16 | 38000 | 10.00 | 106.4 | 2370 | 70 | 70 | 0.0750 | 125.0 | 2450 | 22241 | 2 15/16 | 12 | 4660 | 34 5/8 | 9.44 | 16 1/2 | 12 | 67 | 2.25 | 2 15/16 | LINK BELT SERIES 6800 | 211287 | FLOAT | 2117 | FIXED | 642 | 247 | 314 | 2716 | 1045 STEEL | 0.20 | 0.59 |  |  | ASTM A6 XF-100 | 3/16 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 |  |  |  | 10 | 2716 | 3730 | [5 empty] | 6.4 | 3.8 | 444 | W | TEFC | 1893 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 7.216 | 40.250 |  |  |  | 5041 | 51767 | 19-5-11 |  | Belt |  |  | Yes |  | Yes | [5 empty] | 2 15/16 | [6 empty] | 73 | 15 1/2 | 7 |  | Yes | Ambient Temp F=90 | Size=3612; Design=6195; Arrangement=9H1; % Width=100.0; Discharge=UB; Rotation=CW; CFM=38000; SP=10.00; BHP=106.4; RPM=2370; Max Temp F=70; Effective Wheel Dia=34 11/16; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=19-5-11; Blades=10; Shaft Dia=2 15/16; Brg Centers=12; Critical Speed RPM=4660; BX=16 1/2; STB=12; OH=9.44; STH=2.25; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=444; Motor Position=W; Motor Enclosure=TEFC; Drive=Belt | Open
404783 | GENERAL LINE | CHECK VISION | pdf_vision | Quote Run 404783.pdf |  |  | 404783 | 4412 | 6100 |  |  | 45 | 90.0 | UB | CW |  | 40000 | 19.00 | 149.8 | 1770 | 70 | 70 | 0.0704 | 150.0 | 1800 | 23067 | [8 empty] | 2.81 | [15 empty] | ASTM A572 X-TEN | 5/16 | ASTM A1011-HSLAS | 0.179 (7) | ASTM A572 X-TEN | 1/4 |  |  |  | 10 | 2018 | 2960 | 414 | 352 | 729 | 5.97 | 7.19 |  |  | 445T |  | TEFC | 2231 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 10.371 |  | Not included |  | INCLUDED | 5479 | 44106 | CAST IRON |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 3/8 | [9 empty] | SK-19-72 |  | Ambient Temp F=70; Wheel Weight=414; Thrust=352; WR2 Weight=729; Outlet N x A=29 1/2 IN. X 50 5/8 IN.; Base=445T FR MOTOR; Split Housing=1/4 C.Q. HRS; Wheel Max RPM=2018; Number of Blades=10; RES=2960 CPM | Size=4412; Design=6100; Arrangement=45; % Width=90.0; Discharge=UB; Rotation=CW; CFM=40000; SP=19.00; BHP=149.8; RPM=1770; Max Temp F=70; Blade Material=ASTM A572 X-TEN; Blade Gauge=5/16; Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 (7); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=CAST IRON; Blades=10; STH=2.81; Motor Frame=445T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
404783 | GENERAL LINE | OK | cbc_qt_run_text | Quote Run.txt |  |  | 404783 | 4412 | 6100 |  |  | 4S | 90.0 | UB | CW |  | 40000 | 19.00 | 149.8 | 1770 | 70 | 70 | 0.0704 | 150.0 | 1800 | 23067 | [8 empty] | 2.81 | [15 empty] | ASTM A572 X-TEN | 5/16 | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A572 X-TEN | 1/4 |  |  |  | 10 | 2018 | 2960 | 414 | 352 | 729 | 5.97 | 7.19 |  |  | 445T |  | TEFC | 2231 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 10.371 |  | Not included |  | Included | 5479 | 44106 | 19-5-289 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 3 3/8 | [9 empty] | SK-19-72 |  | Ambient Temp F=70 | Size=4412; Design=6100; Arrangement=4S; % Width=90.0; Discharge=UB; Rotation=CW; CFM=40000; SP=19.00; BHP=149.8; RPM=1770; Max Temp F=70; Blade Material=ASTM A572 X-TEN; Blade Gauge=5/16; Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 ( 7); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=19-5-289; Blades=10; STH=2.81; Motor Frame=445T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
404784 | GENERAL LINE | OK | pdf_vision | Quote Run 404784.pdf |  |  | 404784 | 4412 | 6100 |  |  | 4S | 90.0 | UB | CCW | 23067 | 40000 | 19.00 | 149.8 | 1770 | 70 | 70 | 0.0704 | 150.0 | 1800 | 23067 |  |  | 2960 | [5 empty] | 2.81 | [15 empty] | ASTM A572 X-TEN | 5/16 | ASTM A1011-HSLAS | 0.179 ( 7 ) | ASTM A572 X-TEN | 1/4 |  |  | CAST IRON | 10 | 2018 | 2960 | 414 | 352 | 729 | 5.97 | 7.19 |  |  | 445T |  | TEFC |  | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 10.371 |  | Not included |  | Included | 5479 | 44106 | CAST IRON |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 3 3/8 | [9 empty] | SK-19-72 |  | Ambient Temp F=70; WR2 Weight=729; Thrust=352; Wheel Weight=414; Outlet=29 1/2 IN. X 50 5/8 IN.; Base=445T FR MOTOR | Size=4412; Design=6100; Arrangement=4S; % Width=90.0; Discharge=UB; Rotation=CCW; CFM=40000; SP=19.00; BHP=149.8; RPM=1770; Max Temp F=70; Effective Wheel Dia=23067; Blade Material=ASTM A572 X-TEN; Blade Gauge=5/16; Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 ( 7 ); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Wheel Material=CAST IRON; Hub=CAST IRON; Blades=10; Critical Speed RPM=2960; STH=2.81; Motor Frame=445T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
404795 | GENERAL LINE | OK | pdf_vision | Quote Run 404795.pdf |  |  | 404795 | 2412 | 6195 |  |  | 4S | 70.0 | TH | CW | 23 1/4 | 12314 | 12.99 | 33.8 | 2960 | 113 | 138 | 0.0672 | 33.8 | 3000 | 20108 | 1 7/8 | 22 | [6 empty] | 1.62 | [15 empty] | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) |  |  | C. IRON | 10 | 3861 | 5630 | 61 | 75 | 28 | 2.78 | 4.12 IN |  |  |  |  | ODP |  | 7 GA C.O. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 2.934 |  | Not included |  | Included |  |  | 19-5-1056, Q2 BUSHING 1 7/8 |  | Motor mounted |  |  |  |  | Yes | [17 empty] | Ambient Temp F=63; Wheel Weight=61 LB; Thrust=75 LB; Outlet N x A=15 1/8 IN. x 27 15/16 IN.; Base=200L; Motor=FR MOTOR | Size=2412; Design=6195; Arrangement=4S; % Width=70.0; Discharge=TH; Rotation=CW; CFM=12314; SP=12.99; BHP=33.8; RPM=2960; Max Temp F=138; Effective Wheel Dia=23 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.075 (14); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.105 (12); Wheel Material=C. IRON; Hub=19-5-1056, Q2 BUSHING 1 7/8; Blades=10; Shaft Dia=1 7/8; Brg Centers=22; STH=1.62; Motor Enclosure=ODP; Drive=Motor mounted | Open
404795 | GENERAL LINE | OK | cbc_qt_run_text | Quote Run-Update.txt |  |  | 404795 | 2700 | 6195 |  |  | 4S | 70.0 | TH | CW | 25 5/8 | 12314 | 12.99 | 33.8 | 2960 | 113 | 138 | 0.0672 | 33.8 | 3000 | 20146 | [8 empty] | 1.69 | [15 empty] | ASTM A6 XF-100 | 3/16 | ASTM A6 XF-100 | 1/4 | ASTM A6 XF-100 | 1/4 |  |  |  | 10 | 5184 | 9330 | 125 | 111 | 84 | 3.43 | 4.19 |  |  |  |  | ODP | 631 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 3.523 |  | Not included |  | Included | 1483 | 33439 | 19-5-1056 |  | Motor mounted |  |  | Yes |  | Yes | [7 empty] | Q2 BUSHING 1 7/8 | [9 empty] | Ambient Temp F=63 | Size=2700; Design=6195; Arrangement=4S; % Width=70.0; Discharge=TH; Rotation=CW; CFM=12314; SP=12.99; BHP=33.8; RPM=2960; Max Temp F=138; Effective Wheel Dia=25 5/8; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=1/4; Backplate Material=ASTM A6 XF-100; Backplate Gauge=1/4; Hub=19-5-1056; Blades=10; STH=1.69; Motor Enclosure=ODP; Drive=Motor mounted | Open
404811 | GENERAL LINE | OK | cbc_qt_run_text | 404811_Spark Resistant Type B Qt Run.txt |  |  | 404811 | 24 | 36 |  |  | 4S | 100.0 | UB | CW |  | 11135 | 4.50 | 11.7 | 1770 | 70 | 70 | 0.0720 | 15.0 | 1800 | 12457 | [8 empty] | 2.50 | [15 empty] | ALUM 5052-H32 | 0.125 | ALUM 3003-O | 0.125 | ALUM 5052-H32 | 0.125 |  |  |  | 8 | 2969 | 5870 | 54 | 40 | 20 | 4.46 | 4.75 | [15 empty] | 19-5-27 | [6 empty] | Yes | [5 empty] | 1 5/8 | [11 empty] | Ambient Temp F=70 | Size=24; Design=36; Arrangement=4S; % Width=100.0; Discharge=UB; Rotation=CW; CFM=11135; SP=4.50; BHP=11.7; RPM=1770; Max Temp F=70; Blade Material=ALUM 5052-H32; Blade Gauge=0.125; Sideplate Material=ALUM 3003-O; Sideplate Gauge=0.125; Backplate Material=ALUM 5052-H32; Backplate Gauge=0.125; Hub=19-5-27; Blades=8; STH=2.50 | Open
404873 | GENERAL LINE | OK | cbc_qt_run_text | 404873 quote run.txt |  |  | 404873 | 270 | 51A | 3 |  | 3 |  |  |  |  | 24426 | 12.90 | 75.0 | 2565 |  |  |  |  | 3096 | 17753 | 2 15/16 | 43 | 4028 |  |  |  | 11.63 | 120 |  | 2 15/16 | LINK BELT SERIES 300 | 50160 | FIXED | 977 | FIXED | 92 | 0 | 58 | 3096 | 1045 STEEL | 0.13 | 0.28 |  |  | ASTM A1008 HSLAS | 0.060 (16) | ASTM A1011 CS | 0.075 (14) | [6 empty] | 3096 | 4760 | [5 empty] | 7.4 | [14 empty] | 4-5-38 |  | Belt | [10 empty] | 2 15/16 | [12 empty] | Size=270; Design=51A; Arrangement=3; Class=3; CFM=24426; SP=12.90; BHP=75.0; RPM=2565; Blade Material=ASTM A1008 HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.075 (14); Hub=4-5-38; Shaft Dia=2 15/16; Brg Centers=43; Critical Speed RPM=4028; STB=11.63; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 300; Drive=Belt | Open
405167 | HD-PFD-IAF | OK | cbc_qt_run_text | 361-22-1177 - Hsg and Damper QT Run.txt | DAMPER |  | 405167 | 2412 | 1903 |  | PACKAGED FORCED DRAFT FAN | 4S1 | 100.0 | TH | CW | 25 3/4 | 12029 | 25.20 | 64.3 | 3550 | 138 | 138 | 0.0650 | 75.0 | 3600 | 24245 | [8 empty] | 1.62 | [15 empty] | ASTM A1011-HSLAS | 0.048 (18) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 10 | 3895 | 4870 | 79 | 140 | 40 | 3.22 | 4.12 |  |  | 365T |  | TEFC | 1150 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 3.274 |  | Not included |  |  |  |  | 19-5-1056 |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q1 BUSHING 2 3/8 |  |  |  |  | 44 | 13 15/16 | 10 |  |  | Ambient Temp F=90 | Size=2412; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S1; % Width=100.0; Discharge=TH; Rotation=CW; CFM=12029; SP=25.20; BHP=64.3; RPM=3550; Max Temp F=138; Effective Wheel Dia=25 3/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.048 (18); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=19-5-1056; Blades=10; STH=1.62; Motor Frame=365T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
405203 | HD-PFD-IAF | OK | pdf_vision | 405203_QT RUN.pdf |  |  | 344-22-1122 | 3000 | 1903 |  |  | 4S | 75.0 | DISCH BAU, ROT CW | ROT CW | 31 1/2 | 20000 | 40.00 | 200.0 | 3500 | 70 | 140 | 0.0750 | 200.0 | 3600 | 29688 | 2 3/8 | [7 empty] | 1.94 | BORE 2 3/8 | [14 empty] | ASTM A1011-HSLAS | 0.105 (12) | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  | CAST STEEL | 10 | 4052 | 5410 | 185 | 315 | 160 | 3.86 | 4.19 |  |  | 447TS |  | ODP | 2280 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE | 4.443 |  | Not included |  | Yes | 3902 | 23988 | HUB 19-5-27 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 3/8 | [11 empty] | Ambient Temp F=90; Wheel Weight=185; WR2 Weight=160 | Size=3000; Design=1903; Arrangement=4S; % Width=75.0; Discharge=DISCH BAU, ROT CW; Rotation=ROT CW; CFM=20000; SP=40.00; BHP=200.0; RPM=3500; Max Temp F=140; Effective Wheel Dia=31 1/2; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Wheel Material=CAST STEEL; Hub=HUB 19-5-27; Blades=10; Shaft Dia=2 3/8; STH=1.94; Bearing Size=BORE 2 3/8; Motor Frame=447TS; Motor Enclosure=ODP; Drive=Motor mounted | Open
405206 | GENERAL LINE | OK | cbc_qt_run_text | 405206 - REVISED QUOTE RUN.txt |  |  | 405206 | 445 | 95 |  |  | 9H | 100.0 | UB | CW | 46 9/16 | 45000 | 15.00 | 131.3 | 1492 | 70 | 70 | 0.0750 | 150.0 | 1492 | 20001 | 3 7/16 | 16 | 3324 | 39 | 10.70 | 20 3/8 | 11 5/8 | 103 | 2.94 | 3 7/16 | LINK BELT SERIES 22400 | 147767 | FIXED | 2306 | FIXED | 724 | 0 | 1393 | 1892 | 1045 STEEL | 0.27 | 0.49 | 33 5/8 | 33 1/8 | ASTM A6 XF-100 | 3/8 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  |  | 10 | 1892 | 2760 | [5 empty] | 10.2 | 6.1 | 445 | Z | TEFC | 2231 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 13.033 |  | Included |  | Included | 6244 | 59726 | 19-5-289 |  | Belt |  |  | Yes |  | Yes | [5 empty] | 3 7/16 | [9 empty] | SK-19-72 | Yes | Ambient Temp F=90; Discharge Height (A)=55 13/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=36 1/2; Unitary Base To Cl (LB)=84 1/16; Motor Cl To Fan Cl (LM)=62 1/2; Shaft Height (H)=54 5/8; Total Vert Height (TV)=91 1/8; Max Right of CL to Hsg (RH)=39 15/16; Max Left of CL to Disch (LH)=57 13/16; Mounting Channel (MA)=1 15/16; Base Flange to CL (D)=41 9/16; Drive End of Shaft to CL (K)=48; Mtg Flange to CL (LR)=18 23/32 | Size=445; Design=95; Arrangement=9H; % Width=100.0; Discharge=UB; Rotation=CW; CFM=45000; SP=15.00; BHP=131.3; RPM=1492; Max Temp F=70; Effective Wheel Dia=46 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=3/8; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=19-5-289; Blades=10; Shaft Dia=3 7/16; Brg Centers=16; Critical Speed RPM=3324; BX=20 3/8; STB=11 5/8; OH=10.70; STH=2.94; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 22400; Housing Width (N)=33 5/8; Base to CL (F)=33 1/8; Motor Frame=445; Motor Position=Z; Motor Enclosure=TEFC; Drive=Belt | Open
405206 | GENERAL LINE | OK | pdf_vision | 405206-QT RUN.pdf |  |  | SN405206 | 445 | 95 |  |  | 9HZ | 100.0 | UB | CW | 46 9/16 | 6500 | 15.09 | 131.3 | 1492 | 70 | 70 | 0.0750 | 150.0 | 1492 | 20001 | 3 7/16 | 16 | 3566 | 39 | 10.51 | 20 3/8 | 11 5/8 | 103 | 2.94 | 3 7/16 | LINK BELT SERIES 22400 | 143528 | FIXED | 2337 | FIXED | 671 | 0 | 1197 | 2000 | 1045 STEEL | 0.26 | 0.49 |  |  | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  |  | 10 | 2109 | 2640 | [5 empty] | 10.2 | 6.2 | 445 | Z | TEFC | 2231 | 7 GA C.O. HRS | SK-9-236 HI PRESSURE | 13.033 |  |  |  | Included | 6184 | 59124 | CAST IRON |  | Belt |  |  | Yes |  | Yes | [5 empty] | 3 7/16 | [9 empty] | SK-19-72 | Yes | Ambient Temp F=90; Fan Outlet Area=13.033 FT2; Weight Price=13400; WR2 Weight=119 | Size=445; Design=95; Arrangement=9HZ; % Width=100.0; Discharge=UB; Rotation=CW; CFM=6500; SP=15.09; BHP=131.3; RPM=1492; Max Temp F=70; Effective Wheel Dia=46 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=CAST IRON; Blades=10; Shaft Dia=3 7/16; Brg Centers=16; Critical Speed RPM=3566; BX=20 3/8; STB=11 5/8; OH=10.51; STH=2.94; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 22400; Motor Frame=445; Motor Position=Z; Motor Enclosure=TEFC; Drive=Belt | Open
405333 | GENERAL LINE | OK | cbc_qt_run_text | QUOTE RUN.txt |  |  | 405333 | 22 | A10 |  |  | 4S | 100.0 | UB | CW |  | 10000 | 1.40 | 6.2 | 1750 | 70 | 70 | 0.0750 | 7.5 | 1800 | 11313 | [8 empty] | 2.27 | [15 empty] | ASTM A240 304L SS | 0.060 (16) | ASTM A240 316L SS | 0.105 (12) | ASTM A240 304L SS | 0.105 (12) |  |  |  | 12 | 2475 | 6090 | 74 | 27 | 31 | 4.53 | 4.52 |  |  | 215T |  |  | 160 | 10 GA A240 304L SS | SK-9-236 LOW PRESSURE, 36 IN. CENTERS | 2.945 |  | Not included |  |  |  |  | 19-5-26 |  | Motor mounted |  |  | Yes |  | Yes | [5 empty] | 1 3/8 | [11 empty] | Ambient Temp F=70 | Size=22; Design=A10; Arrangement=4S; % Width=100.0; Discharge=UB; Rotation=CW; CFM=10000; SP=1.40; BHP=6.2; RPM=1750; Max Temp F=70; Blade Material=ASTM A240 304L SS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A240 316L SS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A240 304L SS; Backplate Gauge=0.105 (12); Hub=19-5-26; Blades=12; STH=2.27; Motor Frame=215T; Drive=Motor mounted | Open
405357 | GENERAL LINE | OK | cbc_qt_run_text | QUOTE RUN.txt |  |  | 405357 | 22 | A10 |  |  | 4S | 100.0 | UB | CW |  | 10265 | 1.00 | 6.2 | 1750 | 70 | 70 | 0.0750 | 7.5 | 1800 | 11313 | [8 empty] | 2.27 | [15 empty] | ASTM A240 304L SS | 0.060 (16) | ASTM A240 316L SS | 0.105 (12) | ASTM A240 304L SS | 0.105 (12) |  |  |  | 12 | 2475 | 6090 | 74 | 27 | 31 | 4.53 | 4.52 |  |  | 213T |  |  | 145 | 10 GA A240 304L SS | SK-9-236 LOW PRESSURE, 36 IN. CENTERS | 2.945 |  | Not included |  |  |  |  | 19-5-26 |  | Motor mounted |  |  | Yes |  | Yes | [5 empty] | 1 3/8 | [11 empty] | Ambient Temp F=70 | Size=22; Design=A10; Arrangement=4S; % Width=100.0; Discharge=UB; Rotation=CW; CFM=10265; SP=1.00; BHP=6.2; RPM=1750; Max Temp F=70; Blade Material=ASTM A240 304L SS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A240 316L SS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A240 304L SS; Backplate Gauge=0.105 (12); Hub=19-5-26; Blades=12; STH=2.27; Motor Frame=213T; Drive=Motor mounted | Open
405462 | HD-PFD-IAF | OK | cbc_qt_run_text | 405462_253-22-1318 - 100% Width QT Run.txt |  |  | 405462 | 2000 | 1903 |  | PACKAGED FORCED DRAFT FAN | 4S | 100.0 | TH | CW | 21 | 7200 | 18.00 | 26.2 | 3500 | 70 | 70 | 0.0750 | 30.0 | 3600 | 19792 | [8 empty] | 1.25 | [15 empty] | ASTM A1011-HSLAS | 0.048 (18) | ASTM A1011-HSLAS | 0.048 (18) | ASTM A1011-HSLAS | 0.135 (10) |  |  |  | 10 | 3960 | 5550 | 46 | 62 | 14 | 2.35 | 4.25 |  |  | 286T |  | TEFC | 487 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 2.178 |  | Not included |  | Yes |  |  | 19-5-1055 |  | Motor mounted | Required |  |  |  | Yes | [7 empty] | Q1 BUSHING 1 5/8 | [9 empty] | Ambient Temp F=70 | Size=2000; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S; % Width=100.0; Discharge=TH; Rotation=CW; CFM=7200; SP=18.00; BHP=26.2; RPM=3500; Max Temp F=70; Effective Wheel Dia=21; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.048 (18); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.048 (18); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.135 (10); Hub=19-5-1055; Blades=10; STH=1.25; Motor Frame=286T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
405545 | HD-PFD-IAF | OK | pdf_vision | QT RUN-GMH.pdf |  |  | SN#405545 | 3000 | 1902 |  | PACKAGED FORCED DRAFT FAN | 4S1 | 95.0 | DB | CW |  | 25523 | 8.80 | 113.9 | 3400 | 196 | 196 | 0.0591 | 125.0 | 3400 | 26704 | 1 7/8 | 4.38 | [6 empty] | 1.94 | [15 empty] | ASTM A1011-HSLAS | 0.105 (12) | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  | CAST STEEL | 10 | 3435 | 5070 | 191 | 244 | 164 | 4.38 | 4.19 |  |  | 444TS |  |  | 1515 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 4.769 | 33.000 PER SKE-9-436 | Not included |  |  | 3887 | 47361 | 19-5-27 BORE 2 3/8 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 3/8 | [6 empty] | 59 1/2 | 12 5/8 | 1 |  |  | Ambient Temp F=70; Wheel Weight=191; Thrust=244 LB; WR2 Weight=164 LB-FT2; Outlet N x A=20 1/8 IN. x 34 1/8 IN.; Box B x C=59 1/2 IN. x 12 5/8 IN.; Motor=444TS FR MOTOR; Lifting Lugs=19-9-3733-1; Split Housing=1/4 C.Q. HRS; Outlet Damper=925 IN-LB AT PEAK SP STD AIR; Outlet Damper Axles=52.0 L, 11 IN. FRAME, AREA 5.105 FT2 ON EVASE; Presspin Inlet Damper=1100 IN-LB AT PEAK SP SA; Presspin Inlet Damper Axles=19.9 L, 13 IN. FRAME, AREA 5.217 FT2 ON BOX | Size=3000; Design=1902; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S1; % Width=95.0; Discharge=DB; Rotation=CW; CFM=25523; SP=8.80; BHP=113.9; RPM=3400; Max Temp F=196; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Wheel Material=CAST STEEL; Hub=19-5-27 BORE 2 3/8; Blades=10; Shaft Dia=1 7/8; Brg Centers=4.38; STH=1.94; Motor Frame=444TS; Drive=Motor mounted | Open
405553 | GENERAL LINE | OK | cbc_qt_run_text | 295-22-1168 - Wheel QT Run.txt |  |  | 405553 | 30 | 44A | 1 |  | 1S | 100.0 |  | CW |  | 8000 | 8.00 | 12.1 | 1750 | 230 | 230 | 0.0560 | 15.0 | 1800 | 15254 | [24 empty] | ASTM A1011 CS | 0.075 (14) | ASTM A1011 CS | 0.075 (14) | ASTM A1011-HSLAS | 0.135 (10) |  |  |  | 8 | 2117 | 5030 | [45 empty] | Ambient Temp F=70 | Size=30; Design=44A; Arrangement=1S; % Width=100.0; Rotation=CW; Class=1; CFM=8000; SP=8.00; BHP=12.1; RPM=1750; Max Temp F=230; Blade Material=ASTM A1011 CS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.075 (14); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.135 (10); Blades=8 | Open
405640 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.txt |  |  | 405640 | 3612 | 1904 |  | PACKAGED FORCED DRAFT FAN | 4S | 85.0 | BH | CCW | 40 1/8 | 18362 | 10.80 | 38.9 | 1480 | 100 | 120 | 0.0624 | 50.0 | 1500 | 15767 | [8 empty] | 2.25 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 1/4 |  |  |  | 10 | 2047 | 2560 | 214 | 137 | 305 | 4.27 | 4.50 |  |  |  |  | ODP | 923 | 7 GA C.Q. HRS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 6.819 |  | Not included |  | Included |  |  | 19-5-1057 |  | Motor mounted | Required |  |  |  | Yes | [7 empty] | Q1 BUSHING 2 3/8 | [9 empty] | Ambient Temp F=90 | Size=3612; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S; % Width=85.0; Discharge=BH; Rotation=CCW; CFM=18362; SP=10.80; BHP=38.9; RPM=1480; Max Temp F=120; Effective Wheel Dia=40 1/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Hub=19-5-1057; Blades=10; STH=2.25; Motor Enclosure=ODP; Drive=Motor mounted | Open
405682 | GENERAL LINE | OK | d64_wheel_construction | D64 Wheel Construction (Outer Ring).xlsx | [103 empty] | Fan Size=165; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=50000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.1345 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=165; Outer Ring Thickness=0.1345; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=50000 | Open
405693 | HDX | CHECK VISION | pdf_vision | QT RUN-REV.A.pdf |  |  | SN405693 | 4000 | 2310B |  |  | 8S | 60.0 | BH | CW | 44 | 20735 | 85.2 | 85.2 | 1750 | 70 | 70 | 0.0767 | 100.0 | 1800 | 20735 | 2 3/16 | 12 1/2 | 3691 | 30 1/4 | 7.06 | 7 1/2 | 7 3/4 | M1.5 | 1.75 | 2 3/16 | 6800 | 400000 | FIXED | -88 | FLOAT | 408 | 0 | 364 | 2690 | 1045 STEEL | 0.70 | 0.44 |  |  | ASTM A1011-HSLAS | 0.179 (7) | ASTM A1011-HSLAS | 0.179 (7) | ASTM A1011-HSLAS | 0.179 (7) |  |  |  | 11 | 2843 | 7940 | [7 empty] | 405T |  | TEFC | 1575 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | [5 empty] | 3672 | 45926 | 49-5-145-G BORE 1 15/16 CAST STEEL | FALK T10, SIZE 1090T, BORE 2.188 | Direct |  |  |  | Yes | Yes | [5 empty] | 1 15/16 |  |  | 2.1870 | 2.1860 | 2.1875 | 0.5000 X 0.2500 |  |  |  |  | Yes | Ambient Temp F=70 | Size=4000; Design=2310B; Arrangement=8S; % Width=60.0; Discharge=BH; Rotation=CW; CFM=20735; SP=85.2; BHP=85.2; RPM=1750; Max Temp F=70; Effective Wheel Dia=44; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 (7); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 (7); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 (7); Hub=49-5-145-G BORE 1 15/16 CAST STEEL; Coupling=FALK T10, SIZE 1090T, BORE 2.188; Blades=11; Shaft Dia=2 3/16; Brg Centers=12 1/2; Critical Speed RPM=3691; BX=7 1/2; STB=7 3/4; OH=7.06; STH=1.75; Bearing Size=2 3/16; Bearing Series=6800; Motor Frame=405T; Motor Enclosure=TEFC; Drive=Direct | Open
405698 | GENERAL LINE | OK | cbc_qt_run_text | 358-22-1330 - Shft & Brgs QT Run.txt |  |  | 405698 | 15 | A10 |  |  | 1S | 100.0 | BAU | CW |  | 5000 | 2.50 | 3.8 | 3526 | 500 | 500 | 0.0410 | 7.5 | 3526 |  | 1 15/16 | 16 | 4760 | 34 | 9.94 | 13 7/8 | 5 7/8 |  | 0.00 | 1 15/16 | LINK BELT SERIES 200 | 400000 | FIXED | -61 | FIXED | 72 | 22 |  | 3966 | A240 316 SS | 0.06 | 0.10 | [19 empty] | 4.3 | 3.0 |  |  |  |  | 10 GA C.Q. HRS | SK-9-236 MED PRESSURE, 30 IN. CENTERS | 1.346 | [8 empty] | Belt |  |  |  |  | Yes | [5 empty] | 1 15/16 | [10 empty] | Yes | Ambient Temp F=70 | Size=15; Design=A10; Arrangement=1S; % Width=100.0; Discharge=BAU; Rotation=CW; CFM=5000; SP=2.50; BHP=3.8; RPM=3526; Max Temp F=500; Shaft Dia=1 15/16; Brg Centers=16; Critical Speed RPM=4760; BX=13 7/8; STB=5 7/8; OH=9.94; STH=0.00; Bearing Size=1 15/16; Bearing Series=LINK BELT SERIES 200; Drive=Belt | Open
405810 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.txt |  |  | 405810 | 3000 | 1903 |  | PACKAGED FORCED DRAFT FAN | 4S | 95.0 | BH | CW | 31 1/2 | 21012 | 40.30 | 159.0 | 3550 | 159 | 160 | 0.0630 | 200.0 | 3600 | 29688 | [8 empty] | 1.94 | [15 empty] | ASTM A1011-HSLAS | 0.105 (12) | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  |  | 10 | 3615 | 5300 | 195 | 315 | 172 | 4.40 | 4.19 |  |  | 447TS |  | TEFC | 2850 | 5/16 C.Q. HRS | SK-9-236 HI PRESSURE, 19 IN. CENTERS | 4.769 |  | Not included |  | Included | 4735 | 26321 | 19-5-27 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 3/8 | [11 empty] | Ambient Temp F=70 | Size=3000; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S; % Width=95.0; Discharge=BH; Rotation=CW; CFM=21012; SP=40.30; BHP=159.0; RPM=3550; Max Temp F=160; Effective Wheel Dia=31 1/2; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=19-5-27; Blades=10; STH=1.94; Motor Frame=447TS; Motor Enclosure=TEFC; Drive=Motor mounted | Open
405824 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 405824 | 330 | 51A | 1 |  | 4 | 105.0 |  |  |  | 20703 | 7.51 | 37.5 | 1800 | [5 empty] | 15256 | [8 empty] | 2.94 | [15 empty] | ASTM A1008 HSLAS | 0.060 (16) | ASTM A1011 CS | 0.075 (14) | ASTM A1011 CS | 0.135 (10) |  |  |  | 8 | 2039 | 5280 | 96 | 98 | 81 | 5.89 | 7.88 |  |  | 324T |  | ODP | 550 | [9 empty] | 4-5-15 |  | Motor mounted | Required |  |  |  | Yes | [5 empty] | 2 1/8 | [11 empty] | Ambient Temp F=90 | Size=330; Design=51A; Arrangement=4; % Width=105.0; Class=1; CFM=20703; SP=7.51; BHP=37.5; RPM=1800; Blade Material=ASTM A1008 HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.075 (14); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.135 (10); Hub=4-5-15; Blades=8; STH=2.94; Motor Frame=324T; Motor Enclosure=ODP; Drive=Motor mounted | Open
405954 | GENERAL LINE | OK | d64_wheel_construction | D64 Wheel Construction (Outer Ring).xlsx | [103 empty] | Fan Size=165; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=50000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.1345 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=165; Outer Ring Thickness=0.1345; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=50000 | Open
406000 | GENERAL LINE | OK | d64_wheel_construction | 311-22-1590 D64 Wheel Construction (Inner Ring).xlsx | [103 empty] | Fan Size=200; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=25000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.25 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=200; Outer Ring Thickness=0.25; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=25000 | Open
406071 | GENERAL LINE | OK | cbc_qt_run_text | 317-22-1825 - Shft & Brg QT Run.txt |  |  | 406071 | 24 | B10 |  |  | 1S | 90.0 | BAU | CW |  | 16710 | 9.85 | 39.0 | 3139 | 266 | 266 | 0.0520 | 75.0 | 3200 |  | 2 15/16 | 28 | 4582 | 51 11/16 | 10.25 | 16 7/16 | 10 1/2 | 99 | 0.00 | 2 15/16 | LINK BELT SERIES 300 | 163046 | FIXED | -573 | FIXED | 306 | 0 | 50 | 3436 | 1045 STEEL | 0.10 | 0.35 | [19 empty] | 4.9 | 3.0 |  |  | TEFC |  | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 3.470 | [6 empty] | 19-5-26 |  | Belt |  |  |  |  | Yes | [5 empty] | 2 15/16 | [10 empty] | Yes | Ambient Temp F=70 | Size=24; Design=B10; Arrangement=1S; % Width=90.0; Discharge=BAU; Rotation=CW; CFM=16710; SP=9.85; BHP=39.0; RPM=3139; Max Temp F=266; Hub=19-5-26; Shaft Dia=2 15/16; Brg Centers=28; Critical Speed RPM=4582; BX=16 7/16; STB=10 1/2; OH=10.25; STH=0.00; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 300; Motor Enclosure=TEFC; Drive=Belt | Open
406106 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.txt |  |  | 406106 | 4412 | 1904 |  | PACKAGED FORCED DRAFT FAN | 8S | 95.0 | BH | CW | 48 15/16 | 51159 | 20.00 | 218.9 | 1785 | 100 | 100 | 0.0643 | 250.0 | 1800 | 23067 | 2 15/16 | 14 | 3369 | 33 7/16 | 9.50 | 19 1/16 | 7 3/4 | 64 | 2.81 | 2 15/16 | LINK BELT SERIES 6800 | 357421 | FIXED | -255 | FLOAT | 817 | 0 | 909 | 1800 | 1045 STEEL | 0.50 | 0.45 | 30 1/8 |  | ASTM A1011-HSLAS | 0.060 (16) | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM CQ HRS A36 | 3/8 |  |  |  | 10 | 1800 | 2580 | [7 empty] | 449T |  |  | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 10.591 |  | Included |  | Included |  |  | 19-5-289 |  | Direct |  |  |  |  | Yes | [5 empty] | 2 15/16 |  |  | 2.9370 | 2.9355 | 2.9375 | 0.7500 X 0.3750 |  |  |  |  | Yes | Ambient Temp F=32; Discharge Height (A)=50 5/8; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=33 1/4; Base Width (F)=60 1/2; Shaft Height (H)=59 11/16; Total Vert Height (TV)=95 15/16; Max Right of CL to Hsg (RH)=43 11/16; Max Left of CL to Disch (LH)=33 1/4; Base Flange to CL (D)=92 1/4; Drive End of Shaft to CL (K)=40 13/16; Mtg Flange to CL (LR)=16 31/32 | Size=4412; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=8S; % Width=95.0; Discharge=BH; Rotation=CW; CFM=51159; SP=20.00; BHP=218.9; RPM=1785; Max Temp F=100; Effective Wheel Dia=48 15/16; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 ( 7); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=3/8; Hub=19-5-289; Blades=10; Shaft Dia=2 15/16; Brg Centers=14; Critical Speed RPM=3369; BX=19 1/16; STB=7 3/4; OH=9.50; STH=2.81; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=30 1/8; Motor Frame=449T; Drive=Direct | Open
406123 | HDX | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | SN406123 | 4800 | 4900 |  |  | 88 | 100.0 | UB | CW |  | 6160 | 36.00 | 62.3 | 1775 | 95 | 95 | 0.0698 | 100.0 | 1800 | 22620 | 2 7/16 | 12 1/2 | 3709 | 30 1/8 | 7.42 | 8 1/8 | 7 7/8 | 1.5 | 2.01 | 2 7/16 | 6800 | 196236 | FIXED | -152 | FLOAT | 580 | 0 | 585 | 1865 | 1045 STEEL | 0.53 | 0.32 |  |  | ASTM A572 X-TEN | 3/4 | ASTM A1011-HSLAS | 0.179 (7) | ASTM A572 X-TEN | 1/4 |  |  | CAST STEEL | 11 | 1865 | 2330 | [10 empty] | 1260 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 0.668 |  |  |  |  | 3685 | 49745 | 49-5-145-K BORE 2 3/16 | FALK T10, SIZE 1090T, BORE 2.438 | Direct |  |  |  | Yes | Yes | [5 empty] | 2 3/16 |  |  | 2.4370 | 2.4360 | 2.4375 | 0.6250 X 0.3125 |  |  |  |  | Yes |  | Size=4800; Design=4900; Arrangement=88; % Width=100.0; Discharge=UB; Rotation=CW; CFM=6160; SP=36.00; BHP=62.3; RPM=1775; Max Temp F=95; Blade Material=ASTM A572 X-TEN; Blade Gauge=3/4; Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 (7); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Wheel Material=CAST STEEL; Hub=49-5-145-K BORE 2 3/16; Coupling=FALK T10, SIZE 1090T, BORE 2.438; Blades=11; Shaft Dia=2 7/16; Brg Centers=12 1/2; Critical Speed RPM=3709; BX=8 1/8; STB=7 7/8; OH=7.42; STH=2.01; Bearing Size=2 7/16; Bearing Series=6800; Drive=Direct | Open
406173 | HDX | OK | pdf_vision | QT RUN-Pricing.pdf |  |  | SN5148-HDX | 3612 | 1807 |  | IRT FAN | 9H | 100.0 | DISCH BAU | ROT CW |  | 20000 | 8.50 | 93.0 | 1840 | 550 | 550 | 0.0332 | 125.0 | 1840 | 17582 | 2 15/16 | 22 1/2 | 3231 | 52 | 11.82 | 16 | 15 1/4 | M1.5 | 2.88 | 2 15/16 | LINK BELT SERIES 22400 | 130595 | FIXED | 1740 | FIXED | 423 | 0 | 146 | 2145 | 1045 STEEL | 0.45 | 0.94 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.179 (7) |  |  | CAST STEEL | 12 | 2145 | 2790 | [5 empty] | 8.3 | 7.7 | 405 | Z | ODP | 1260 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 4.275 |  |  |  | Included | 3708 | 46285 | 19 5-11 |  | Belt |  |  |  | Yes | Yes | [5 empty] | 2 11/16 | [10 empty] | Yes | Ambient Temp F=90 | Size=3612; Design=1807; Fan Type=IRT FAN; Arrangement=9H; % Width=100.0; Discharge=DISCH BAU; Rotation=ROT CW; CFM=20000; SP=8.50; BHP=93.0; RPM=1840; Max Temp F=550; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 (7); Wheel Material=CAST STEEL; Hub=19 5-11; Blades=12; Shaft Dia=2 15/16; Brg Centers=22 1/2; Critical Speed RPM=3231; BX=16; STB=15 1/4; OH=11.82; STH=2.88; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 22400; Motor Frame=405; Motor Position=Z; Motor Enclosure=ODP; Drive=Belt | Open
406173 | HDX | OK | pdf_vision | QT RUN-4800.pdf |  |  | SN406173 | 3000 | 4800 |  | REPLACEMENT ROTOR 4800 RT | 9H | 100.0 | DISCH BAU | ROT CW |  | 25000 | 28.00 | 147.7 | 2773 | 70 | 70 | 0.0750 | 150.0 | 2805 | 22030 | 2 15/16 | 22 | 4060 | 46 | 10.97 | 16 | 12 |  |  | 2 15/16 | LINK BELT 6800 | 108724 | FLOAT | 2507 | FIXED | 523 | 79 | 108 | 3000 |  | 0.23 | 0.70 |  |  | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A572 X-TEN |  |  |  | WDFN2 | 12 | 3500 | 6160 | [5 empty] | 5.5 | 4.0 | 444 | W | ODP |  | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 3.306 |  |  |  | Included | 3645 | 47831 | HUB 19-5-27 |  | Belt |  |  |  | Yes | Yes | [5 empty] | 2 11/16 | [10 empty] | Yes | Ambient Temp F=90; Hub Material=CAST STEEL | Size=3000; Design=4800; Fan Type=REPLACEMENT ROTOR 4800 RT; Arrangement=9H; % Width=100.0; Discharge=DISCH BAU; Rotation=ROT CW; CFM=25000; SP=28.00; BHP=147.7; RPM=2773; Max Temp F=70; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 ( 7); Backplate Material=ASTM A572 X-TEN; Wheel Material=WDFN2; Hub=HUB 19-5-27; Blades=12; Shaft Dia=2 15/16; Brg Centers=22; Critical Speed RPM=4060; BX=16; STB=12; OH=10.97; Bearing Size=2 15/16; Bearing Series=LINK BELT 6800; Motor Frame=444; Motor Position=W; Motor Enclosure=ODP; Drive=Belt | Open
406235 | GENERAL LINE | OK | cbc_qt_run_text | 406235 quote run (run test).txt |  |  | 406235 | 20 | 36 | 3 |  | 9H | 100.0 | BH | CCW |  | 8000 | 6.00 | 11.3 | 2619 | 500 | 500 | 0.0400 | 15.0 | 2619 | 14796 | 1 15/16 | 8 | 3820 | 27 1/4 | 9.81 | 14 13/16 | 6 7/8 | 23 | 2.04 | 1 15/16 | LINK BELT SERIES 200 | 171517 | FIXED | 187 | FIXED | 129 | 0 | 29 | 3183 | 1045 STEEL | 0.16 | 0.20 |  |  | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A1011 CS | 0.105 (12) | ASTM CQ HRS A36 | 1/4 |  |  |  | 12 | 3229 | 9560 | [5 empty] | 5.8 | 3.0 | [13 empty] | 4-5-38 |  | Belt |  |  |  |  | Yes | [5 empty] | 1 15/16 | [11 empty] | Ambient Temp F=70 | Size=20; Design=36; Arrangement=9H; % Width=100.0; Discharge=BH; Rotation=CCW; Class=3; CFM=8000; SP=6.00; BHP=11.3; RPM=2619; Max Temp F=500; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Hub=4-5-38; Blades=12; Shaft Dia=1 15/16; Brg Centers=8; Critical Speed RPM=3820; BX=14 13/16; STB=6 7/8; OH=9.81; STH=2.04; Bearing Size=1 15/16; Bearing Series=LINK BELT SERIES 200; Drive=Belt | Open
406238 | HD-PFD-IAF | OK | pdf_vision | 317-22-1929 - QT Run 1903 Wheel with Nose.pdf |  |  | 317-22-1929 | 3612 | 1903 |  | PACKAGED FORCED DRAFT FAN | 4S | 110.0 | PCT, DISCH TH, ROT CW | CW | 38 5/16 | 26000 | 11.00 | 60.6 | 1620 | 70 | 70 | 0.0737 | 75.0 | 1800 | 18060 | RE SK-9-105 | 19-5-1057 | 17200 | [5 empty] | 2.25 | [15 empty] | ASTM A1011-HSLAS | 0.060 (16) | ASTM A1011-HSLAS | 0.135 (10) | ASTM CQ HRS A36 | 1/4 |  |  |  | 10 | 2498 | 3120 | 206 | 173 | 261 | 5.07 | 4.50 |  |  | 365T |  | ODP | 1150 | 7 GA C.Q. HRS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 7.468 |  | Not included |  | Included |  |  | 1/2 BUSHING 2 3/8, C. IRON |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q1 BUSHING 2 3/8 | [9 empty] | Ambient Temp F=90; Blades/2 RIB=0.060 (16); Nose=0.375; Blades Count=10; Wheel Weight=206; Thrust=173; WR2=261 LB-FT2; Outlet N x A=25 7/8 IN. x 41 9/16 IN.; Base=365T FR MOTOR; Motor Mounting Included=True; Motor Weight=1150; Frame Stiffeners=SK-9-236 MED PRESSURE, 24 IN. CENTERS; Flanged Inlet Included=True; Housing 7 GA C.Q. HRS=True; Fan Outlet Area=7.468 FT2 | Size=3612; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S; % Width=110.0; Discharge=PCT, DISCH TH, ROT CW; Rotation=CW; CFM=26000; SP=11.00; BHP=60.6; RPM=1620; Max Temp F=70; Effective Wheel Dia=38 5/16; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Hub=1/2 BUSHING 2 3/8, C. IRON; Blades=10; Shaft Dia=RE SK-9-105; Brg Centers=19-5-1057; Critical Speed RPM=17200; STH=2.25; Motor Frame=365T; Motor Enclosure=ODP; Drive=Motor mounted | Open
406244 | HDX | OK | pdf_vision | QT RUN-REVISED CLEARANCE FIT HUB KEYED.pdf |  |  | SN406244 | 10 | 1903 |  |  | 3D2 | 105.0 | 105.0 PCT | DISCH TH, ROT CCW | 93 7/16 | 384030 | 6.80 | 554.0 | 899 | 70 | 800 | 0.0302 | 600.0 | 900 | 22019 | 21 | 228 7/8 | 1265 |  |  |  | 25.82 |  |  | 10 |  |  | FIXED | 12979 | FLOAT | 12342 | 0 | 49256 | 903 | 1045 STEEL | 0.09 | 0.06 |  |  | ASTM A6 XF-100 | 3/16 | ASTM A572 X-TEN | 3/8 | ASTM A572 X-TEN | 3/4 |  |  | CAST STEEL | [23 empty] | 19-5-2272 | FALK T10, SIZE 1120T, BORE 4 7/16 | NON-NEMA MOTOR |  |  |  | Yes | [9 empty] | 4.4370 | 4.4355 | 4.4375 | 1.0000 X 0.5000 | [5 empty] | Ambient Temp F=70 | Size=10; Design=1903; Arrangement=3D2; % Width=105.0; Discharge=105.0 PCT; Rotation=DISCH TH, ROT CCW; CFM=384030; SP=6.80; BHP=554.0; RPM=899; Max Temp F=800; Effective Wheel Dia=93 7/16; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=3/8; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/4; Wheel Material=CAST STEEL; Hub=19-5-2272; Coupling=FALK T10, SIZE 1120T, BORE 4 7/16; Shaft Dia=21; Brg Centers=228 7/8; Critical Speed RPM=1265; STB=25.82; Bearing Size=10; Drive=NON-NEMA MOTOR | Open
406244 | HDX | NO FIELDS | pdf | QT RUN.pdf | [105 empty] | Open
406416 | GENERAL LINE | OK | d64_wheel_construction | 406416_333-18-2686 D64 Wheel Construction (Outer Ring) (1).xlsx | [103 empty] | Fan Size=150; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=50000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.1345 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=150; Outer Ring Thickness=0.1345; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=50000 | Open
406465 | GENERAL LINE | OK | cbc_qt_run_text | GENERIC Quote Run.txt |  |  | 406465 | 402 | 51A | 2 |  | 4 |  |  |  |  | 30000 | 15.70 | 58.6 | 1800 | [5 empty] | 18555 | [8 empty] | 3.44 | [15 empty] | ASTM A1008 HSLAS | 0.060 (16) | ASTM A1011 CS | 0.075 (14) | ASTM A1011 CS | 0.179 ( 7) |  |  |  | 8 | 1864 | 4850 | 158 | 218 | 212 | 6.98 | 7.07 |  |  | 364T |  | ODP | 835 | [9 empty] | 4-5-39 |  | Motor mounted | Required |  |  |  | Yes | [5 empty] | 2 3/8 | [11 empty] | Ambient Temp F=70 | Size=402; Design=51A; Arrangement=4; Class=2; CFM=30000; SP=15.70; BHP=58.6; RPM=1800; Blade Material=ASTM A1008 HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.075 (14); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.179 ( 7); Hub=4-5-39; Blades=8; STH=3.44; Motor Frame=364T; Motor Enclosure=ODP; Drive=Motor mounted | Open
406678 | HDX | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | 360-22-1454RP | 6000 | 1903 |  |  | 88 | 92.0 | DISCH BH | ROT CW | 63 | 64260 | 18.00 | 229.7 | 1178 | 450 | 450 | 0.0436 | 250.0 | 1178 | 19429 | 3 7/16 | 20 | 1779 | 49 15/16 | 15.68 | 27 9/16 | 12 3/4 | 1.5 131 | 4.12 | 7/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -435 | FLOAT | 1337 | 0 | 2211 | 1203 |  | 0.86 | 0.48 |  |  | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.075 (14) | ASTM A572 X-TEN | 5/16 |  |  | CAST IRON | 10 | 1203 | 1500 | [7 empty] | 449T |  |  | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 18.840 |  |  |  | Yes | 11301 | 94557 | BORE 3 3/16 | FALK T10, SIZE 1100T, BORE 3.438 | Direct |  |  |  | Yes | Yes | [5 empty] | 3 3/16 | [10 empty] | Yes | Ambient Temp F=90 | Size=6000; Design=1903; Arrangement=88; % Width=92.0; Discharge=DISCH BH; Rotation=ROT CW; CFM=64260; SP=18.00; BHP=229.7; RPM=1178; Max Temp F=450; Effective Wheel Dia=63; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.075 (14); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Wheel Material=CAST IRON; Hub=BORE 3 3/16; Coupling=FALK T10, SIZE 1100T, BORE 3.438; Blades=10; Shaft Dia=3 7/16; Brg Centers=20; Critical Speed RPM=1779; BX=27 9/16; STB=12 3/4; OH=15.68; STH=4.12; Bearing Size=7/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=449T; Drive=Direct | Open
406678 | HDX | OK | pdf_vision | QT RUN A36 Backplate.pdf |  |  | 360-22-1454RP | 6000 | 1903 |  |  | 8S | 92.0 | BH | CW | 63 | 64260 | 18.00 | 229.7 | 1178 | 90 | 450 | 0.0436 | 250.0 | 1178 | 19429 | 3 7/16 | 20 | 1816 | 50 3/8 | 15.68 | 28 | 12 | 3/4 | 131 | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -411 | FLOAT | 1282 | 0 | 2073 | 1241 |  | 0.84 | 0.48 |  |  | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.135 (10) | ASTM CO HRS A36 | 5/16 |  |  | CAST IRON | 10 | 1241 | 1550 | [7 empty] | 449T |  |  | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 18.840 |  |  |  | Yes | 11285 | 93557 | HUB 19-5-17 | FALK T10, SIZE 1100T, BORE 3.438 NOT INCL. | DRIVE-FIXED |  |  |  | Yes | Yes | [16 empty] | Yes | Ambient Temp F=90 | Size=6000; Design=1903; Arrangement=8S; % Width=92.0; Discharge=BH; Rotation=CW; CFM=64260; SP=18.00; BHP=229.7; RPM=1178; Max Temp F=450; Effective Wheel Dia=63; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM CO HRS A36; Backplate Gauge=5/16; Wheel Material=CAST IRON; Hub=HUB 19-5-17; Coupling=FALK T10, SIZE 1100T, BORE 3.438 NOT INCL.; Blades=10; Shaft Dia=3 7/16; Brg Centers=20; Critical Speed RPM=1816; BX=28; STB=12; OH=15.68; STH=131; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=449T; Drive=DRIVE-FIXED | Open
406693 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.txt |  |  | 406693 | 3000 | 1903 |  |  | 8S | 95.0 | UB | CCW | 31 1/2 | 11300 | 5.00 | 11.7 | 1750 | 400 | 450 | 0.0420 | 25.0 | 1800 | 14844 | 2 3/16 | 12 | 3409 | 28 | 9.39 | 15 3/4 | 5 5/8 |  | 1.94 | 2 3/16 | LINK BELT SERIES 300 | 400000 | FIXED | -90 | FIXED | 267 | 79 | 109 | 1831 | A240 304 SS | 0.21 | 0.11 | 20 1/8 |  | ASTM A240 304L SS | 0.060 (16) | ASTM A240 304L SS | 0.105 (12) | ASTM A240 304L SS | 1/4 |  |  |  | 10 | 1831 | 2290 | [7 empty] | 284T |  |  | 355 | 10 GA A240 304L SS | SK-9-236 MED PRESSURE, 30 IN. CENTERS | 4.769 |  | Included |  | Included | 1530 | 41048 | 19-5- |  | Direct |  |  | Yes |  | Yes | [5 empty] | 2 3/16 |  |  | 2.1870 | 2.1860 | 2.1875 | 0.5000 X 0.2500 |  |  |  |  | Yes | Ambient Temp F=90; Discharge Height (A)=34 1/8; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=24 3/8; Base Width (F)=44 1/4; Shaft Height (H)=32 5/8; Total Vert Height (TV)=57; Max Right of CL to Hsg (RH)=36 1/8; Max Left of CL to Disch (LH)=24 5/8; Base Flange to CL (D)=57 3/4; Drive End of Shaft to CL (K)=33 3/8; Mtg Flange to CL (LR)=12 9/16 | Size=3000; Design=1903; Arrangement=8S; % Width=95.0; Discharge=UB; Rotation=CCW; CFM=11300; SP=5.00; BHP=11.7; RPM=1750; Max Temp F=450; Effective Wheel Dia=31 1/2; Blade Material=ASTM A240 304L SS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A240 304L SS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A240 304L SS; Backplate Gauge=1/4; Hub=19-5-; Blades=10; Shaft Dia=2 3/16; Brg Centers=12; Critical Speed RPM=3409; BX=15 3/4; STB=5 5/8; OH=9.39; STH=1.94; Bearing Size=2 3/16; Bearing Series=LINK BELT SERIES 300; Housing Width (N)=20 1/8; Motor Frame=284T; Drive=Direct | Open
406841 | HD-PFD-IAF | CHECK VISION | pdf_vision | QUOTE RUN.pdf |  |  | SN406841 | 5414 | 5500 | 8S |  | 8S | 100.0 | BH | CW | 53 3/4 | 5314 | 20.00 | 145.8 | 1800 | 518 | 518 | 0.0390 | 200.0 | 1800 | 25329 | 3 7/16 | 16 | 3506 | 40 5/16 | 11.25 | 18 3/4 | 9 7/8 |  | 2.19 | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -211 | FLOAT | 828 | 0 | 1039 | 1947 | 1045 STEEL | 0.46 | 0.26 |  |  | ASTM A1011-HSLAS | 0.179 (7) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A572 X-TEN | 5/16 |  |  |  |  | 1965 | [8 empty] | 447T |  | ODP | 2280 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 7.701 |  |  |  | Included | 8052 | 90139 | HUB 23-5-424 BORE(3 3/16) CAST STEEL | FALK T10, SIZE 1100T, BORE 3.438 NOT INCL. | MOTOR WEIGHT AND MOUNTING, MOTOR PRICE NOT INCL. |  | Required |  | Yes | Yes | [8 empty] | 3.4370 | 3.4355 | 3.4375 | 0.8750 X 0.4375 |  |  |  | SK-55-11 | Yes | Ambient Temp F=90 | Size=5414; Design=5500; Arrangement=8S; % Width=100.0; Discharge=BH; Rotation=CW; Class=8S; CFM=5314; SP=20.00; BHP=145.8; RPM=1800; Max Temp F=518; Effective Wheel Dia=53 3/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 (7); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=HUB 23-5-424 BORE(3 3/16) CAST STEEL; Coupling=FALK T10, SIZE 1100T, BORE 3.438 NOT INCL.; Shaft Dia=3 7/16; Brg Centers=16; Critical Speed RPM=3506; BX=18 3/4; STB=9 7/8; OH=11.25; STH=2.19; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=447T; Motor Enclosure=ODP; Drive=MOTOR WEIGHT AND MOUNTING, MOTOR PRICE NOT INCL. | Open
406906 | HDX | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | SN406906 | 6000 | 5500 |  |  | 781 | 100.0 | PCT | CW | 59 1/2 | 63649 | 37.20 | 476.9 | 1780 | 142 | 180 | 0.0643 | 500.0 | 1800 | 28039 | 4 3/16 | 60 1/8 | 2844 | 1734 |  |  | 9.38 |  | 2.38 | 3 3/16 | 6800 | 400000 | FLOAT | 692 | FIXED | 255 | 729 | 1734 | 1936 | 1045 STEEL | 0.36 | 0.78 |  |  | ASTM A1011-HSLAS | 0.179 (7) | ASTM A1011-HSLAS | 0.179 (7) | ASTM A572 X-TEN | 5/16 |  |  | CAST STEEL | 16 | 1936 | [10 empty] | ODP | 3460 | 3/8 C.Q. HRS | SK-9-236 HI PRESSURE, 19 IN. CENTERS | 9.421 |  | Included | 3.00 |  | 13865 | 132861 | 49- | FALK T10, SIZE 1100T | Direct |  |  |  | Yes | [6 empty] | 4 3/16 |  |  | 3.1870 | 3.1855 |  | 0.7500 X 0.3750 | 81 3/4 | 25 13/16 | 789 | SK-55-11 | Yes | Ambient Temp F=70 | Size=6000; Design=5500; Arrangement=781; % Width=100.0; Discharge=PCT; Rotation=CW; CFM=63649; SP=37.20; BHP=476.9; RPM=1780; Max Temp F=180; Effective Wheel Dia=59 1/2; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 (7); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 (7); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Wheel Material=CAST STEEL; Hub=49-; Coupling=FALK T10, SIZE 1100T; Blades=16; Shaft Dia=4 3/16; Brg Centers=60 1/8; Critical Speed RPM=2844; STB=9.38; STH=2.38; Bearing Size=3 3/16; Bearing Series=6800; Motor Enclosure=ODP; Drive=Direct | Open
406940 | HD-PFD-IAF | OK | cbc_qt_run_text | 253-22-2450 - WHEEL QT RUN.pdf |  |  | 406940 | 4014 | 1902 |  |  | 4S | 50.0 | BAU | CW |  | 13520 | 18.00 | 50.1 | 1770 | 70 | 95 | 0.0750 | 75.0 | 1800 | 18967 | [8 empty] | 2.50 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A572 X-TEN | 1/4 |  |  |  | 10 | 2167 | 2710 | 228 | 221 | 295 | 3.79 | 6.38 |  |  | 365T |  | ODP | 920 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 7.278 |  | Not included |  | Yes | 2709 | 26459 | 19-5-16 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 3/8 | [11 empty] | Ambient Temp F=70 | Size=4014; Design=1902; Arrangement=4S; % Width=50.0; Discharge=BAU; Rotation=CW; CFM=13520; SP=18.00; BHP=50.1; RPM=1770; Max Temp F=95; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=19-5-16; Blades=10; STH=2.50; Motor Frame=365T; Motor Enclosure=ODP; Drive=Motor mounted | Open
407003 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 407003 | 20 | 36 | 3 |  | 1S | 80.0 | TH | CW |  | 7500 | 14.00 | 23.7 | 2923 | 70 | 400 | 0.0750 | 25.0 | 2923 | 16514 | 1 15/16 | 8 | 4151 | 27 3/4 | 10.23 | 14 11/16 | 7 | 23 | 2.04 | 1 15/16 | LINK BELT SERIES 22400 | 400000 | FIXED | -535 | FIXED | 337 | 0 | 22 | 3459 | 1045 STEEL | 0.16 | 0.31 |  |  | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A1011 CS | 0.105 (12) | ASTM A1011 CS | 0.135 (10) |  |  |  | 12 | 3647 | [6 empty] | 5.2 | 3.0 | [13 empty] | 4-5-38 |  | Belt |  |  |  |  | Yes | [5 empty] | 1 15/16 | [11 empty] | Ambient Temp F=90 | Size=20; Design=36; Arrangement=1S; % Width=80.0; Discharge=TH; Rotation=CW; Class=3; CFM=7500; SP=14.00; BHP=23.7; RPM=2923; Max Temp F=400; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.135 (10); Hub=4-5-38; Blades=12; Shaft Dia=1 15/16; Brg Centers=8; Critical Speed RPM=4151; BX=14 11/16; STB=7; OH=10.23; STH=2.04; Bearing Size=1 15/16; Bearing Series=LINK BELT SERIES 22400; Drive=Belt | Open
407004 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 407004 | 20 | 36 | 3 |  | 1S | 80.0 | TH | CCW |  | 7500 | 14.00 | 23.7 | 2923 | 70 | 400 | 0.0750 | 25.0 | 2923 | 16514 | 1 15/16 | 8 | 4151 | 27 3/4 | 10.23 | 14 11/16 | 7 | 23 | 2.04 | 1 15/16 | LINK BELT SERIES 22400 | 400000 | FIXED | -535 | FIXED | 337 | 0 | 22 | 3459 | 1045 STEEL | 0.16 | 0.31 |  |  | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A1011 CS | 0.105 (12) | ASTM A1011 CS | 0.135 (10) |  |  |  | 12 | 3647 | [6 empty] | 5.2 | 3.0 | [13 empty] | 4-5-38 |  | Belt |  |  |  |  | Yes | [5 empty] | 1 15/16 | [11 empty] | Ambient Temp F=90 | Size=20; Design=36; Arrangement=1S; % Width=80.0; Discharge=TH; Rotation=CCW; Class=3; CFM=7500; SP=14.00; BHP=23.7; RPM=2923; Max Temp F=400; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.135 (10); Hub=4-5-38; Blades=12; Shaft Dia=1 15/16; Brg Centers=8; Critical Speed RPM=4151; BX=14 11/16; STB=7; OH=10.23; STH=2.04; Bearing Size=1 15/16; Bearing Series=LINK BELT SERIES 22400; Drive=Belt | Open
407014 | GENERAL LINE | OK | cbc_qt_run_text | revised QT Run for 90% Width.txt |  |  | 407014 | 5414 | 6195 |  |  | 8S | 90.0 | BAU | CCW | 51 9/16 | 79239 | 13.30 | 164.0 | 1780 | 100 | 100 | 0.0680 | 300.0 | 1800 | 26715 | 3 15/16 | 16 | 3339 | 39 5/8 | 11.72 | 22 11/16 | 10 1/8 | 137 | 3.38 | 3 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -508 | FLOAT | 1562 | 0 | 2251 | 2000 | 1045 STEEL | 0.30 | 0.23 | 35 7/8 |  | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 5/16 | ASTM A572 X-TEN | 1/2 |  |  |  | 10 | 2081 | 3440 | [7 empty] | 449T |  |  | 2600 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 15.384 |  | Included |  | Included | 8955 | 93502 | 19-5-12 | FALK T10 | Direct |  | Required | Yes | [7 empty] | 3 15/16 |  |  | 3.9370 | 3.9355 | 3.9375 | 1.0000 X 0.5000 |  |  |  | SK-19-72 | Yes | Ambient Temp F=70; Discharge Height (A)=61 3/4; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=40 3/8; Base Width (F)=72 1/2; Shaft Height (H)=66 1/4; Total Vert Height (TV)=105 7/8; Max Right of CL to Hsg (RH)=73 5/8; Max Left of CL to Disch (LH)=48 11/16; Base Flange to CL (D)=95 3/4; Drive End of Shaft to CL (K)=48 13/16; Mtg Flange to CL (LR)=20 3/16 | Size=5414; Design=6195; Arrangement=8S; % Width=90.0; Discharge=BAU; Rotation=CCW; CFM=79239; SP=13.30; BHP=164.0; RPM=1780; Max Temp F=100; Effective Wheel Dia=51 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=5/16; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Hub=19-5-12; Coupling=FALK T10; Blades=10; Shaft Dia=3 15/16; Brg Centers=16; Critical Speed RPM=3339; BX=22 11/16; STB=10 1/8; OH=11.72; STH=3.38; Bearing Size=3 15/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=35 7/8; Motor Frame=449T; Drive=Direct | Open
407015 | HD-PFD-IAF | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | SN#407015 | 3000 | 5800 |  |  | 8S | 100.0 | BH | CW | 28 1/8 | 28000 | 69.8 | 75.0 | 3550 | 90 | 300 | 0.0629 | 75.0 | 3600 | 26507 | 2 11/16 | 12 | 6799 | 30 1/8 | 8.78 | 12 | 7 5/8 | 49 | 1.38 | 2 11/16 | 300 | 400000 | FIXED | -18 | FLOAT | 181 | 0 | 51 | 3600 | 1045 STEEL | 0.12 | 0.10 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) |  |  | CAST STEEL | 10 | 4365 | [8 empty] | 365TS |  |  | 920 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 19 IN. CENTERS | 1.172 |  |  |  | Included | 2475 | 40949 | 23-5-423 | FALK T10, SIZE 1080T, BORE 2.688 | Direct |  | Required |  |  | Yes | [5 empty] | 2 11/16 |  |  | 2.6870 | 2.6860 | 2.6875 | 0.6250 X 0.3125 |  |  |  |  | Yes | Ambient Temp F=90 | Size=3000; Design=5800; Arrangement=8S; % Width=100.0; Discharge=BH; Rotation=CW; CFM=28000; SP=69.8; BHP=75.0; RPM=3550; Max Temp F=300; Effective Wheel Dia=28 1/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.135 (10); Wheel Material=CAST STEEL; Hub=23-5-423; Coupling=FALK T10, SIZE 1080T, BORE 2.688; Blades=10; Shaft Dia=2 11/16; Brg Centers=12; Critical Speed RPM=6799; BX=12; STB=7 5/8; OH=8.78; STH=1.38; Bearing Size=2 11/16; Bearing Series=300; Motor Frame=365TS; Drive=Direct | Open
407076 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.txt |  |  | 407076 | 3612 | 1904 |  | PACKAGED FORCED DRAFT FAN | 8S | 90.0 | TH | CW | 40 1/8 | 24942 | 14.83 | 81.8 | 1775 | 100 | 100 | 0.0750 | 100.0 | 1800 | 18920 | 2 7/16 | 12 | 4574 | 27 3/4 | 7.66 | 15 5/16 | 7 1/2 | 37 | 2.25 | 2 7/16 | LINK BELT SERIES 300 | 400000 | FIXED | -111 | FIXED | 372 | 197 | 312 | 2164 | 1045 STEEL | 0.35 | 0.32 |  |  | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 1/4 |  |  |  | 10 | 2481 | [8 empty] | 405T |  | TEFC | 1575 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 6.963 |  |  |  | Yes |  |  | 19-5-1057 | FALK T10 | Direct |  |  |  |  | Yes | [7 empty] | Q1 BUSHING 2 7/16 | [8 empty] | Yes | Ambient Temp F=90 | Size=3612; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=8S; % Width=90.0; Discharge=TH; Rotation=CW; CFM=24942; SP=14.83; BHP=81.8; RPM=1775; Max Temp F=100; Effective Wheel Dia=40 1/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Hub=19-5-1057; Coupling=FALK T10; Blades=10; Shaft Dia=2 7/16; Brg Centers=12; Critical Speed RPM=4574; BX=15 5/16; STB=7 1/2; OH=7.66; STH=2.25; Bearing Size=2 7/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=405T; Motor Enclosure=TEFC; Drive=Direct | Open
407171 | GENERAL LINE | OK | cbc_qt_run_text | wheel QT Run.txt |  |  | 407171 | 20 | 36 | 3 |  | 1S | 100.0 | UB | CW |  | 6000 | 7.50 | 9.4 | 2122 | 70 | 70 | 0.0750 | 10.0 | 2122 | 11989 | 2 3/16 | 8 | 5292 | 27 1/8 | 10.09 | 14 13/16 | 6 3/4 |  | 2.04 | 2 3/16 | LINK BELT SERIES 200 | 400000 | FIXED | -48 | FIXED | 144 | 26 | 21 | 2756 | A240 304 SS | 0.07 | 0.03 |  |  | ASTM A240 304L SS | 3/16 | ASTM A240 304L SS | 0.105 (12) | ASTM A240 304L SS | 0.135 (10) |  |  |  | 8 | 2756 | 4220 | [20 empty] | 4-5-145 | FALK G20 | Direct |  |  | Yes |  | Yes | [5 empty] | 2 3/16 | [11 empty] | Ambient Temp F=90 | Size=20; Design=36; Arrangement=1S; % Width=100.0; Discharge=UB; Rotation=CW; Class=3; CFM=6000; SP=7.50; BHP=9.4; RPM=2122; Max Temp F=70; Blade Material=ASTM A240 304L SS; Blade Gauge=3/16; Sideplate Material=ASTM A240 304L SS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A240 304L SS; Backplate Gauge=0.135 (10); Hub=4-5-145; Coupling=FALK G20; Blades=8; Shaft Dia=2 3/16; Brg Centers=8; Critical Speed RPM=5292; BX=14 13/16; STB=6 3/4; OH=10.09; STH=2.04; Bearing Size=2 3/16; Bearing Series=LINK BELT SERIES 200; Drive=Direct | Open
407171 | GENERAL LINE | OK | cbc_qt_run_text | shaft and Brgs QT Run.txt |  |  | 407171 | 222 | 51A | 3 |  | 1 |  |  |  |  | 6000 | 7.50 | 9.4 | 2122 |  |  |  |  | 2756 |  | 2 7/16 | 14 | 9190 | 28 11/16 | 6.39 | 11 7/16 | 5 7/8 |  | 0.00 | 2 7/16 | LINK BELT SERIES 200 | 400000 | FIXED | 12 | FIXED | 100 | 28 | 22 | 2756 | A240 304 SS | 0.04 | 0.02 | [35 empty] | FALK G20 | Direct | Required |  | Yes |  | Yes | [5 empty] | 2 7/16 |  |  | 2.4370 | 2.4360 | 2.4375 | 0.6250 X 0.3125 | [5 empty] | Ambient Temp F=90 | Size=222; Design=51A; Arrangement=1; Class=3; CFM=6000; SP=7.50; BHP=9.4; RPM=2122; Coupling=FALK G20; Shaft Dia=2 7/16; Brg Centers=14; Critical Speed RPM=9190; BX=11 7/16; STB=5 7/8; OH=6.39; STH=0.00; Bearing Size=2 7/16; Bearing Series=LINK BELT SERIES 200; Drive=Direct | Open
407189 | GENERAL LINE | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | SN#407189 | 22.250 | 6195 | 88 |  | 88 | 80.0 | UB | ROT CW | 21 1/8 | 7978 | 10.99 | 17.7 | 3200 | 70 | 302 | 0.0537 | 20.0 | 3200 | 19479 | 2 11/16 | 12 | 6233 | 30 3/16 | 9.13 | 13 1/16 | 7 1/8 | 49 | 1.62 | 2 11/16 | LINK BELT SERIES 200 | 400000 | FIXED | -29 | FIXED | 198 | 58 |  | 3600 | 1045 STEEL | 0.07 | 0.03 |  |  | ASTM A6 XF-100 | 3/16 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 |  |  | CAST IRON | 10 | 5814 | 11350 | [7 empty] | 256T |  |  | 250 | 10 GA A607 X-TEN | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 2.511 |  |  |  | Included |  |  | 2.6875 | FALK T10, SIZE 10B0T, BORE 2.688 | Direct |  |  | Yes |  | Yes | [5 empty] | 2 11/16 |  |  | 2.6870 | 2.6860 | 2.6875 | 0.6250 X 0.3125 |  |  |  |  | Yes | Ambient Temp F=70 | Size=22.250; Design=6195; Arrangement=88; % Width=80.0; Discharge=UB; Rotation=ROT CW; Class=88; CFM=7978; SP=10.99; BHP=17.7; RPM=3200; Max Temp F=302; Effective Wheel Dia=21 1/8; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Wheel Material=CAST IRON; Hub=2.6875; Coupling=FALK T10, SIZE 10B0T, BORE 2.688; Blades=10; Shaft Dia=2 11/16; Brg Centers=12; Critical Speed RPM=6233; BX=13 1/16; STB=7 1/8; OH=9.13; STH=1.62; Bearing Size=2 11/16; Bearing Series=LINK BELT SERIES 200; Motor Frame=256T; Drive=Direct | Open
407191 | GENERAL LINE | OK | cbc_qt_run_text | QT Run-407191.txt |  |  | 407191 | 4900 | 6195 |  |  | 8S | 115.0 | UB | CW | 46 9/16 | 40291 | 8.83 | 73.4 | 1201 | 84 | 302 | 0.0724 | 75.0 | 1201 | 14636 | 3 7/16 | 16 | 2601 | 40 3/4 | 14.84 | 25 1/4 | 9 3/8 | 107 | 2.94 | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -342 | FLOAT | 936 | 0 | 968 | 1364 | 1045 STEEL | 0.26 | 0.14 | 35 3/8 |  | ASTM A6 XF-100 | 3/16 | ASTM A572 X-TEN | 3/16 | ASTM A572 X-TEN | 1/4 |  |  |  | 10 | 1364 | 1880 | [7 empty] | 405T |  |  | 1260 | 7 GA A607 X-TEN | SK-9-236 MED PRESSURE, 30 IN. CENTERS | 13.711 |  | Included |  | Included | 5119 | 81183 | 19-5-289 | FALK T10 | Direct |  |  | Yes |  | Yes | [5 empty] | 3 7/16 |  |  | 3.4370 | 3.4355 | 3.4375 | 0.8750 X 0.4375 |  |  |  |  | Yes | Ambient Temp F=70; Discharge Height (A)=55 13/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=36 1/2; Base Width (F)=66 1/4; Shaft Height (H)=54 5/8; Total Vert Height (TV)=91 1/8; Max Right of CL to Hsg (RH)=39 15/16; Max Left of CL to Disch (LH)=57 13/16; Base Flange to CL (D)=82 13/16; Drive End of Shaft to CL (K)=50 5/8; Mtg Flange to CL (LR)=19 19/32 | Size=4900; Design=6195; Arrangement=8S; % Width=115.0; Discharge=UB; Rotation=CW; CFM=40291; SP=8.83; BHP=73.4; RPM=1201; Max Temp F=302; Effective Wheel Dia=46 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=3/16; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=19-5-289; Coupling=FALK T10; Blades=10; Shaft Dia=3 7/16; Brg Centers=16; Critical Speed RPM=2601; BX=25 1/4; STB=9 3/8; OH=14.84; STH=2.94; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=35 3/8; Motor Frame=405T; Drive=Direct | Open
407192 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN-407192.txt |  |  | 407192 | 4900 | 6195 |  |  | 8S | 100.0 | BAU | CW | 46 9/16 | 33795 | 6.62 | 44.8 | 1184 | 164 | 302 | 0.0549 | 60.0 | 1200 | 16087 | 3 7/16 | 16 | 2473 | 40 | 14.65 | 24 1/8 | 8 7/8 |  | 2.94 | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -373 | FLOAT | 1003 | 0 | 1067 | 1334 | A240 304 SS | 0.23 | 0.10 | 33 5/8 |  | ASTM A240 304L SS | 5/16 | ASTM A240 304L SS | 3/16 | ASTM A240 304L SS | 3/16 |  |  |  | 10 | 1334 | 1670 | [7 empty] | 404T |  |  | 1145 | 3/16 A240 304L SS | SK-9-236 MED PRESSURE, 30 IN. CENTERS | 13.033 |  | Included |  | Included |  |  | 19-5-1168 | FALK T10 | Direct |  |  | Yes |  | Yes | [5 empty] | 3 7/16 |  |  | 3.4370 | 3.4355 | 3.4375 | 0.8750 X 0.4375 |  |  |  |  | Yes | Ambient Temp F=70; Discharge Height (A)=55 13/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=36 1/2; Base Width (F)=66 1/4; Shaft Height (H)=58 11/16; Total Vert Height (TV)=94 9/16; Max Right of CL to Hsg (RH)=44 1/16; Max Left of CL to Disch (LH)=66 11/16; Base Flange to CL (D)=79 11/16; Drive End of Shaft to CL (K)=49; Mtg Flange to CL (LR)=18 23/32 | Size=4900; Design=6195; Arrangement=8S; % Width=100.0; Discharge=BAU; Rotation=CW; CFM=33795; SP=6.62; BHP=44.8; RPM=1184; Max Temp F=302; Effective Wheel Dia=46 9/16; Blade Material=ASTM A240 304L SS; Blade Gauge=5/16; Sideplate Material=ASTM A240 304L SS; Sideplate Gauge=3/16; Backplate Material=ASTM A240 304L SS; Backplate Gauge=3/16; Hub=19-5-1168; Coupling=FALK T10; Blades=10; Shaft Dia=3 7/16; Brg Centers=16; Critical Speed RPM=2473; BX=24 1/8; STB=8 7/8; OH=14.65; STH=2.94; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=33 5/8; Motor Frame=404T; Drive=Direct | Open
407254 | HDX | OK | pdf_vision | 6105 qt run 7d2.pdf |  |  | 400426 | 3000 | 1903 |  |  | 7D2 | 80.0 | 0 | CW | 31 1/2 | 10777 | 3.45 | 7.4 | 985 | 70 | 80 | 0.0750 | 40.0 | 1000 |  | 2 15/16 | 63 3/4 | 1522 | 74.75 | 58.50 | 31.88 | 8.12 | 147 | 1060 | 2 15/16 | LINK BELT SERIES 300 | 400000 | FIXED | 220 | FIXED | 185 | 0 | 144 | 1522 | 1045 STEEL. | 0.21 | 0.13 | [21 empty] | 364T |  | ODP |  |  | SK-9-236 LOW PRESSURE, 36 IN. CENTERS | 8.176 | [7 empty] | FALK T10, SIZE 108OT, BORE 2 15/16 NOT INCL. | Direct |  |  |  |  | Yes | [8 empty] | 2.9370 | 2.9355 |  | 0.7500 X 0.3750 | 54 | 11 3/8 |  |  | Yes | Ambient Temp F=90; Wheel Weight Specified=241; Wheel Hub Nominal Bore=2.9375; Wheel Hub Max Bore=2.9390; Wheel Hub Min Bore=2.9380; Wheel Hub Keyway Width=0.7510 (MIN) - 0.7540 (MAX); Wheel Hub Keyway Depth=0.3750; Coupling Reference=SKE-9-356; Rotor Weight=144 LB-FT2; Material=1045 STEEL; Bearing L10 Hr (Other-Fixed)=400000; Bearing L10 Hr (Drive-Fixed)=400000; Fan Outlet Area=8.176 FT2 | Size=3000; Design=1903; Arrangement=7D2; % Width=80.0; Discharge=0; Rotation=CW; CFM=10777; SP=3.45; BHP=7.4; RPM=985; Max Temp F=80; Effective Wheel Dia=31 1/2; Coupling=FALK T10, SIZE 108OT, BORE 2 15/16 NOT INCL.; Shaft Dia=2 15/16; Brg Centers=63 3/4; Critical Speed RPM=1522; BX=31.88; STB=8.12; OH=58.50; STH=1060; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=364T; Motor Enclosure=ODP; Drive=Direct | Open
407254 | HDX | OK | pdf_vision | 6105 DW-QT RUNS_10-6-22.pdf |  |  | ORDER400426 | 3000 | 1903 |  |  | 3D2 | 80.0 | TH | CW | 31 1/2 | 10777 | 3.45 | 7.4 | 985 | 70 | 80 | 0.0750 | 40.0 | 1000 |  | 2 15/16 | 74 3/4 | 1178 | 85.75 | 64.50 | 37.38 | 8.12 | 168 | 1168 | 2 15/16 | LINK BELT SERIES 300 | 400000 | FIXED | 231 | FIXED | 196 | 0 | 144 | 1177 | 1045 STEEL | 0.24 | 0.13 | [10 empty] | 1045 STEEL | [15 empty] | SK-9-236 LOW PRESSURE, 36 IN. CENTERS | 8.176 | [6 empty] | 2.9375 | FALK T10, SIZE 1080T, BORE 2 15/16 | Direct | [13 empty] | 2.9370 | 2.9355 |  | 0.7500 X 0.3750 | 54 11 3/8 |  |  |  | Yes | Ambient Temp F=90; Rotor Wr2=144 LB-FT2; MTL=1045 STEEL | Size=3000; Design=1903; Arrangement=3D2; % Width=80.0; Discharge=TH; Rotation=CW; CFM=10777; SP=3.45; BHP=7.4; RPM=985; Max Temp F=80; Effective Wheel Dia=31 1/2; Wheel Material=1045 STEEL; Hub=2.9375; Coupling=FALK T10, SIZE 1080T, BORE 2 15/16; Shaft Dia=2 15/16; Brg Centers=74 3/4; Critical Speed RPM=1178; BX=37.38; STB=8.12; OH=64.50; STH=1168; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 300; Drive=Direct | Open
407288 | HD-PFD-IAF | OK | pdf_vision | QT RUN.pdf |  |  | SN407288 (311-22-884) IC | 3000 | 1904 |  |  | 4S | 85.0 | DISCH TH | ROT CW | 33 | 25671 | 28.00 | 158.3 | 3500 | 150 | 150 | 0.0590 | 200.0 | 3600 | 31102 | [8 empty] | 1.94 | [15 empty] | ASTM A572 X-TEN | 1/4 | ASTM A1011-HSLAS | 0.075 (14) | ASTM A572 X-TEN | 3/8 |  |  | CAST STEEL | 10 | 3792 | 4960 | 213 | 360 | 210 | 3.97 | 4.19 |  |  | 447T |  | TEFC | 2850 | 1/2 C.Q. HRS | SK-9-236 HI PRESSURE, 18 IN. CENTERS | 4.591 |  | Not included |  | Yes | 4927 | 34568 | CAST STEEL |  | Motor mounted | Required | Required |  |  | Yes | [5 empty] | 2 3/8 | [11 empty] | Ambient Temp F=90; Wheel Weight=213; Number of Blades=10; Outlet Dimensions=19 3/8 IN. x 34 1/8 IN.; Thrust=360 | Size=3000; Design=1904; Arrangement=4S; % Width=85.0; Discharge=DISCH TH; Rotation=ROT CW; CFM=25671; SP=28.00; BHP=158.3; RPM=3500; Max Temp F=150; Effective Wheel Dia=33; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.075 (14); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Wheel Material=CAST STEEL; Hub=CAST STEEL; Blades=10; STH=1.94; Motor Frame=447T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
407348 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 407348 | 4412 | 6195 |  |  | 8S | 50.0 | TAU | CW | 42 1/4 | 20000 | 16.00 | 66.0 | 1770 | 100 | 100 | 0.0698 | 75.0 | 1800 | 19922 | 2 11/16 | 14 | 3463 | 34 3/16 | 8.93 | 16 3/4 | 8 3/8 | 55 | 2.81 | 2 11/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -181 | FLOAT | 621 | 0 | 591 | 2304 | 1045 STEEL | 0.26 | 0.18 | 25 1/4 |  | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 |  |  |  | 10 | 2304 | 5170 | [7 empty] | 365T |  |  | 920 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 8.877 |  | Included |  | Included | 3731 | 41923 | 19-5-289 | FALK T10 | Direct |  |  | Yes |  | Yes | [5 empty] | 2 11/16 |  |  | 2.6870 | 2.6860 | 2.6875 | 0.6250 X 0.3125 |  |  |  |  | Yes | Ambient Temp F=70; Discharge Height (A)=50 5/8; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=33 1/4; Base Width (F)=60 1/2; Shaft Height (H)=43 1/2; Total Vert Height (TV)=104 3/16; Max Right of CL to Hsg (RH)=32 9/16; Max Left of CL to Disch (LH)=47 3/8; Base Flange to CL (D)=68 3/4; Drive End of Shaft to CL (K)=39 1/8; Mtg Flange to CL (LR)=15 5/8 | Size=4412; Design=6195; Arrangement=8S; % Width=50.0; Discharge=TAU; Rotation=CW; CFM=20000; SP=16.00; BHP=66.0; RPM=1770; Max Temp F=100; Effective Wheel Dia=42 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=19-5-289; Coupling=FALK T10; Blades=10; Shaft Dia=2 11/16; Brg Centers=14; Critical Speed RPM=3463; BX=16 3/4; STB=8 3/8; OH=8.93; STH=2.81; Bearing Size=2 11/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=25 1/4; Motor Frame=365T; Drive=Direct | Open
407349 | HD-PFD-IAF | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | SN#407349 | 4900 | 5500 |  | RAINBOW FERTILIZER; DRYER FAN | 98 | 100.0 | TH | CCW | 51 7/8 | 23200 | 8.00 | 187.0 | 1780 | 210 | 235 | 0.0562 | 200.0 | 1800 | 24446 | 2 15/16 | 16 | 3733 | 37 3/16 | 9.78 | 16 1/8 | 8 3/4 | 72 | 2.00 | 2 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -122 | FLOAT | 539 | 0 | 627 | 2360 | 1045 STEEL | 0.44 | 0.41 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 (7) |  |  | CAST STEEL | 16 | 2360 | [8 empty] | 447T |  |  | 2280 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 6.293 |  | Included | 3.00 | Included | 5967 | 60479 | 49-5-145-G BORE 2 15/16 | FALK T10, SIZE 1090T, BORE 2.938 NOT INCL. | 447T FR MOTOR |  |  |  |  | Yes | [5 empty] | 2 15/16 |  |  | 2.9370 | 2.9355 | 2.9375 | 0.7500 X 0.3750 |  |  |  |  | Yes | Ambient Temp F=70 | Size=4900; Design=5500; Fan Type=RAINBOW FERTILIZER; DRYER FAN; Arrangement=98; % Width=100.0; Discharge=TH; Rotation=CCW; CFM=23200; SP=8.00; BHP=187.0; RPM=1780; Max Temp F=235; Effective Wheel Dia=51 7/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 (7); Wheel Material=CAST STEEL; Hub=49-5-145-G BORE 2 15/16; Coupling=FALK T10, SIZE 1090T, BORE 2.938 NOT INCL.; Blades=16; Shaft Dia=2 15/16; Brg Centers=16; Critical Speed RPM=3733; BX=16 1/8; STB=8 3/4; OH=9.78; STH=2.00; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=447T; Drive=447T FR MOTOR | Open
407350 | HD-PFD-IAF | OK | pdf_vision | QT RUN.pdf |  |  | SN#407350 | 4900 | 5500 |  | RAINBOW FERTILIZER; COOLER FAN | 8S | 100.0 | TH | CCW | 48 7/8 | 32000 | 26.0 | 163.9 | 1780 | 70 | 175 | 0.0620 | 200.0 | 1800 | 23032 | 2 7/16 | 16 | 3623 | 34 15/16 | 7.61 | 14 | 8 5/8 | 46 | 2.00 | 2 7/16 | 6800 | 400000 | FIXED | -75 | FLOAT | 442 | 0 | 518 | 2375 | 1045 STEEL | 0.72 | 0.70 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 (7) |  |  | CAST STEEL | 16 | 2375 | [8 empty] | 447T |  |  | 2280 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 6.293 |  |  |  | Included | 5840 | 59423 | 49-5-145-G BORE 2 7/16 | FALK T10, SIZE 1090T, BORE 2.438 | Direct |  |  |  |  | Yes | [5 empty] | 2 7/16 |  |  | 2.4370 | 2.4360 | 2.4375 | 0.6250 X 0.3125 |  |  |  |  | Yes | Ambient Temp F=70 | Size=4900; Design=5500; Fan Type=RAINBOW FERTILIZER; COOLER FAN; Arrangement=8S; % Width=100.0; Discharge=TH; Rotation=CCW; CFM=32000; SP=26.0; BHP=163.9; RPM=1780; Max Temp F=175; Effective Wheel Dia=48 7/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 (7); Wheel Material=CAST STEEL; Hub=49-5-145-G BORE 2 7/16; Coupling=FALK T10, SIZE 1090T, BORE 2.438; Blades=16; Shaft Dia=2 7/16; Brg Centers=16; Critical Speed RPM=3623; BX=14; STB=8 5/8; OH=7.61; STH=2.00; Bearing Size=2 7/16; Bearing Series=6800; Motor Frame=447T; Drive=Direct | Open
407475 | GENERAL LINE | OK | cbc_qt_run_text | WHEEL QT RUN.txt |  |  | 407475 | 22 | B10 | 4 |  | 9H | 100.0 | UB | CW |  | 14500 | 19.00 | 56.1 | 3320 | 150 | 150 | 0.0635 | 75.0 | 3320 | 20867 | 2 3/16 | 14 | 5031 | 33 1/2 | 8.18 | 13 11/16 | 10 1/2 | 36 | 2.27 | 2 3/16 | LINK BELT SERIES 6800 | 400000 | FIXED | 1048 | FIXED | 276 | 96 | 36 | 3800 | 1045 STEEL | 0.20 | 0.82 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 8 | 4049 | [6 empty] | 4.6 | 3.7 | 365T | W |  | 920 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 2.945 |  |  |  | Included |  |  | 19-5-26 |  | Belt |  |  |  |  | Yes | [5 empty] | 2 3/16 | [10 empty] | Yes | Ambient Temp F=70 | Size=22; Design=B10; Arrangement=9H; % Width=100.0; Discharge=UB; Rotation=CW; Class=4; CFM=14500; SP=19.00; BHP=56.1; RPM=3320; Max Temp F=150; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=19-5-26; Blades=8; Shaft Dia=2 3/16; Brg Centers=14; Critical Speed RPM=5031; BX=13 11/16; STB=10 1/2; OH=8.18; STH=2.27; Bearing Size=2 3/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=365T; Motor Position=W; Drive=Belt | Open
407497 | HDX | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | SN407497 | 6300 | 5500 |  |  | 781 | 100.0 | PCT | CW | 63 3/4 | 30042 | 30030 | 663.6 | 1780 | 90 | 180 | 0.0650 | 700.0 | 1800 | 30042 | 5 1/4 | 65 7/16 | 3017 | 79.81 | 52.62 | 14.86 | 23.62 | 10.62 | 2.56 | 3 15/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 1109 | FIXED | 431 | 945 | 3300 | 1851 | 1045 STEEL | 0.27 | 0.58 |  |  | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/2 |  |  | CAST STEEL | 16 | 1851 | [10 empty] | ODP | 7000 | 3/8 C.Q. HRS | SK-9-236 HI PRESSURE, 18 IN. CENTERS | 10.393 |  |  |  |  | 21821 | 185140 | 5.2500 | FALK T10, SIZE 1110T, BORE 3 15/16 | Direct |  | Required |  | Yes | [6 empty] | 5 1/4 |  |  | 3.9370 | 3.9355 |  | 1.0000 X 0.5000 | 86 | 27 1/16 | 789 | SK-55-11 | Yes | Ambient Temp F=90 | Size=6300; Design=5500; Arrangement=781; % Width=100.0; Discharge=PCT; Rotation=CW; CFM=30042; SP=30030; BHP=663.6; RPM=1780; Max Temp F=180; Effective Wheel Dia=63 3/4; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Wheel Material=CAST STEEL; Hub=5.2500; Coupling=FALK T10, SIZE 1110T, BORE 3 15/16; Blades=16; Shaft Dia=5 1/4; Brg Centers=65 7/16; Critical Speed RPM=3017; BX=14.86; STB=23.62; OH=52.62; STH=2.56; Bearing Size=3 15/16; Bearing Series=LINK BELT SERIES 6800; Motor Enclosure=ODP; Drive=Direct | Open
407551 | HD-PFD-IAF | OK | cbc_qt_run_text | QUOTE RUN.txt |  |  | 407551 | 4412 | 1904 |  | PACKAGED FORCED DRAFT FAN | 8S | 60.0 | UB | CW | 48 15/16 | 26140 | 28.00 | 148.0 | 1770 | 95 | 95 | 0.0705 | 200.0 | 1800 | 23067 | 2 11/16 | 14 | 3263 | 34 11/16 | 8.65 | 17 5/16 | 8 7/8 | 56 | 2.81 | 2 11/16 | LINK BELT SERIES 6800 | 219631 | FIXED | -208 | FLOAT | 738 | 0 | 841 | 1800 | 1045 STEEL | 0.53 | 0.48 | 26 3/8 |  | ASTM A1011-HSLAS | 0.060 (16) | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM CQ HRS A36 | 3/8 |  |  |  | 10 | 1800 | 2690 | [7 empty] | 447T |  |  | 2280 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 9.272 |  | Included |  | Included |  |  | 19-5-289 | FALK T10 | Direct |  |  |  |  | Yes | [5 empty] | 2 11/16 |  |  | 2.6870 | 2.6860 | 2.6875 | 0.6250 X 0.3125 |  |  |  |  | Yes | Ambient Temp F=70; Discharge Height (A)=50 5/8; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=33 1/4; Base Width (F)=60 1/2; Shaft Height (H)=47 3/16; Total Vert Height (TV)=80 7/16; Max Right of CL to Hsg (RH)=36 1/4; Max Left of CL to Disch (LH)=52 5/8; Base Flange to CL (D)=82 13/16; Drive End of Shaft to CL (K)=40 3/16; Mtg Flange to CL (LR)=16 3/16 | Size=4412; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=8S; % Width=60.0; Discharge=UB; Rotation=CW; CFM=26140; SP=28.00; BHP=148.0; RPM=1770; Max Temp F=95; Effective Wheel Dia=48 15/16; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 ( 7); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=3/8; Hub=19-5-289; Coupling=FALK T10; Blades=10; Shaft Dia=2 11/16; Brg Centers=14; Critical Speed RPM=3263; BX=17 5/16; STB=8 7/8; OH=8.65; STH=2.81; Bearing Size=2 11/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=26 3/8; Motor Frame=447T; Drive=Direct | Open
407616 | GENERAL LINE | OK | cbc_qt_run_text | 407474_407474 quote run.txt |  |  | 407474 | 27 | B10 | 4 |  | 9H | 100.0 | UB | CW |  | 24000 | 22.00 | 108.3 | 2925 | 150 | 150 | 0.0635 | 150.0 | 2925 | 22309 | 2 11/16 | 13 | 4342 | 36 13/16 | 11.44 | 18 1/16 | 12 1/8 | 59 | 2.62 | 2 11/16 | LINK BELT SERIES 6800 | 104335 | FIXED | 2153 | FIXED | 685 | 162 | 87 | 3115 | 1045 STEEL | 0.25 | 0.99 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 12 | 3115 | [6 empty] | 5.2 | 5.1 | [13 empty] | 19-5-26 |  | Belt |  |  |  |  | Yes | [5 empty] | 2 11/16 | [11 empty] | Ambient Temp F=70 | Size=27; Design=B10; Arrangement=9H; % Width=100.0; Discharge=UB; Rotation=CW; Class=4; CFM=24000; SP=22.00; BHP=108.3; RPM=2925; Max Temp F=150; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=19-5-26; Blades=12; Shaft Dia=2 11/16; Brg Centers=13; Critical Speed RPM=4342; BX=18 1/16; STB=12 1/8; OH=11.44; STH=2.62; Bearing Size=2 11/16; Bearing Series=LINK BELT SERIES 6800; Drive=Belt | Open
407929 | GENERAL LINE | OK | d64_wheel_construction | 333-18-2686 D64 Wheel Construction (Outer Ring).xlsx | [103 empty] | Fan Size=150; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=50000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.1345 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=150; Outer Ring Thickness=0.1345; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=50000 | Open
407930 | GENERAL LINE | OK | d64_wheel_construction | 333-18-2686 D64 Wheel Construction (Outer Ring).xlsx | [103 empty] | Fan Size=150; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=50000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.1345 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=150; Outer Ring Thickness=0.1345; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=50000 | Open
407931 | GENERAL LINE | OK | d64_wheel_construction | 333-18-2686 D64 Wheel Construction (Outer Ring).xlsx | [103 empty] | Fan Size=150; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=50000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.1345 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=150; Outer Ring Thickness=0.1345; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=50000 | Open
407932 | GENERAL LINE | OK | d64_wheel_construction | 333-18-2686 D64 Wheel Construction (Outer Ring).xlsx | [103 empty] | Fan Size=150; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=50000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.1345 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=150; Outer Ring Thickness=0.1345; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=50000 | Open
408001 | HDX | CHECK VISION | pdf_vision | QT RUN-408001.pdf |  |  | SN408001 | 5414 | 1903 |  |  | 7SL | 85.0 | 0 | CCW | 56 15/16 | 26843 | 373.5 | 400.0 | 1780 | 90 | 180 | 0.0654 | 400.0 | 1800 | 26843 | 5 1/2 | 75 15/16 | 2767 | 2382 | 94.44 | 64.25 | 9.25 | 16.73 | 3.38 | 3 7/16 | 6800 | 400000 | FLOAT | 1007 | FIXED | 454 | 842 | 2382 | 1908 | 1045 STEEL | 0.15 | 0.50 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/2 |  |  | CAST STEEL | 10 | 1921 | 2790 | [7 empty] | 28 |  | ODP | 5000 | 3/8 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 15.062 |  | Included | 3.00 |  | 21775 | 220002 | 19-5-12 | THOMAS 71 SIZE 462 BORE 3 7/16 | DUAL DRIVE FAN - TURBINE LOCATED ON DRIVE SIDE (CAFT) TO WHEEL |  |  |  | Yes | [9 empty] | 3.4370 | 3.4355 |  | 0.8750 X 0.4375 | 98 | 20 3/4 | 789 | SK-19-72 | Yes | Ambient Temp F=90 | Size=5414; Design=1903; Arrangement=7SL; % Width=85.0; Discharge=0; Rotation=CCW; CFM=26843; SP=373.5; BHP=400.0; RPM=1780; Max Temp F=180; Effective Wheel Dia=56 15/16; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Wheel Material=CAST STEEL; Hub=19-5-12; Coupling=THOMAS 71 SIZE 462 BORE 3 7/16; Blades=10; Shaft Dia=5 1/2; Brg Centers=75 15/16; Critical Speed RPM=2767; BX=64.25; STB=9.25; OH=94.44; STH=3.38; Bearing Size=3 7/16; Bearing Series=6800; Motor Frame=28; Motor Enclosure=ODP; Drive=DUAL DRIVE FAN - TURBINE LOCATED ON DRIVE SIDE (CAFT) TO WHEEL | Open
408015 | HDX | CHECK VISION | pdf_vision | QT RUN-CO#1.pdf |  |  | SN#408015 | 5414 | 5500 |  | FD FAN W/ PGR | ARR 781,100.0 | 100.0 | TH |  | 57 | 51350 | 30.20 | 331.5 | 1780 | 172 | 180 | 0.0569 | 350.0 | 1800 | 26861 | 3 11/16 | 56 1/8 | 2505 |  |  |  | 9.38 |  | 2.19 | 3 3/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 614 | FIXED | 224 | 578 | 1593 | 2004 | 4140 STEEL | 0.38 | 0.55 |  |  | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  | CAST STEEL | 16 | 2466 | [8 empty] | 449T |  |  | 2600 | 1/4 A572 X-TEN | SK-9-236 HI PRESSURE, 19 IN. CENTERS | 7.701 |  | Included | 3.00 |  | 10157 | 139277 | 23-5-424 | FALK T10, SIZE 1100T | Direct |  |  |  | Yes | [9 empty] | 3.1870 | 3.1855 |  | 0.7500 X 0.3750 | 74 | 23 5/16 | 789 | SK-55-11 | Yes |  | Size=5414; Design=5500; Fan Type=FD FAN W/ PGR; Arrangement=ARR 781,100.0; % Width=100.0; Discharge=TH; CFM=51350; SP=30.20; BHP=331.5; RPM=1780; Max Temp F=180; Effective Wheel Dia=57; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Wheel Material=CAST STEEL; Hub=23-5-424; Coupling=FALK T10, SIZE 1100T; Blades=16; Shaft Dia=3 11/16; Brg Centers=56 1/8; Critical Speed RPM=2505; STB=9.38; STH=2.19; Bearing Size=3 3/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=449T; Drive=Direct | Open
408015 | HDX | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | SN#408015 | 5414 | 5500 |  |  | 781,100.0 PCT | 100.0 | TH | ROT CW | 57 | 51350 | 30.20 | 331.5 | 1780 | 172 | 180 | 0.0569 | 350.0 | 1800 | 26861 | 3 11/16 | 56 1/8 | 2505 |  |  |  | 9.38 |  | 2.19 | 3 3/16 | 6800 | 400000 | FLOAT | 614 | FIXED | 224 | 578 | 1593 | 2004 | 1045 STEEL | 0.38 | 0.55 |  |  | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  | OMIT STEEL | 16 | 2166 | [8 empty] | 449T |  |  | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 19 IN. CENTERS | 7.701 |  | Included | 3.00 |  | 10142 | 115543 | 23-5-424 | FALK T10, SIZE 1100T, BORE 3 3/16 | DRIVE-FLOAT |  |  |  | Yes | [9 empty] | 3.1870 | 3.1855 |  | 0.7500 X 0.3750 | 74 | 23 5/16 | 789 | SK-55-11 | Yes | Ambient Temp F=90 | Size=5414; Design=5500; Arrangement=781,100.0 PCT; % Width=100.0; Discharge=TH; Rotation=ROT CW; CFM=51350; SP=30.20; BHP=331.5; RPM=1780; Max Temp F=180; Effective Wheel Dia=57; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Wheel Material=OMIT STEEL; Hub=23-5-424; Coupling=FALK T10, SIZE 1100T, BORE 3 3/16; Blades=16; Shaft Dia=3 11/16; Brg Centers=56 1/8; Critical Speed RPM=2505; STB=9.38; STH=2.19; Bearing Size=3 3/16; Bearing Series=6800; Motor Frame=449T; Drive=DRIVE-FLOAT | Open
408202 | HDX | OK | pdf_vision | QT RUN.pdf |  |  | 6874-HDX | 6300 | 4800 |  |  | 8S1 | 80.0 | 0 | CCW |  | 68502 | 14.00 | 203.0 | 1180 | 90 | 285 | 0.0534 | 250.0 | 1200 | 19792 | 3 3/16 | 28 | 2194 | 50 1/8 | 10.09 | 21 | 8 15/16 |  | 2.44 | 3 3/16 | 6800 | 6800 | FIXED | -182 | FLOAT | 1152 | 0 | 2355 | 1411 | 1045 STEEL | 0.93 | 0.60 |  |  | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 3/8 |  |  | CAST IRON | 12 | 1411 | 1780 | [7 empty] | 449T |  | ODP | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 15.500 |  |  |  |  | 14017 | 130560 | 2 15/16 | FALK G20, SIZE 1030G | Direct |  |  |  | Yes | Yes | [5 empty] | 2 15/16 | [6 empty] | 86 7/8 | 29 | 1 |  | Yes | Ambient Temp F=90 | Size=6300; Design=4800; Arrangement=8S1; % Width=80.0; Discharge=0; Rotation=CCW; CFM=68502; SP=14.00; BHP=203.0; RPM=1180; Max Temp F=285; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Wheel Material=CAST IRON; Hub=2 15/16; Coupling=FALK G20, SIZE 1030G; Blades=12; Shaft Dia=3 3/16; Brg Centers=28; Critical Speed RPM=2194; BX=21; STB=8 15/16; OH=10.09; STH=2.44; Bearing Size=3 3/16; Bearing Series=6800; Motor Frame=449T; Motor Enclosure=ODP; Drive=Direct | Open
408289 | HDX | CHECK VISION | pdf_vision | 408289 QT RUN REV 1.pdf |  |  | SN#408289 | 4014 | 1903 |  |  | 781 | 90.0 | TAU,ROT CW,BOX 0 | CW | 42 1/4 | 33109 | 34.9 BHP | 34.9 | 1775 | 799 | 799 | 0.0292 | 50.0 | 1800 | 19916 | 4 7/16 | 66 3/16 | 2839 | 75.31 |  |  | 6.38 |  | 2.50 | SIZE 2 3/16 | LINK BELT SERIES 6800 | 400000 | FIXED | 476 | FLOAT | 238 | 0 | 559 LB-FT2 | 2200 |  | 0.15 | 0.25 |  |  | ASTM A1011-HSLAS | 0.105 (12) | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  | CAST STEEL | 10 | 2200 | 2820 | [7 empty] | 326T |  |  | 610 |  | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 8.510 |  | Included | 3.00 |  | 6007 | 121483 | 19-5-219 | THOMAS 71 SIZE 300, BORE 2 3/16 | Direct | Required |  |  | Yes | Yes | [8 empty] | 2.1870 | 2.1860 |  | 0.5000 X 0.2500 | 73 | 15 1/2 | 789 |  | Yes | Ambient Temp F=90 F; Customer=JOHN ZINK; Cooling Wheels=4-2-38 | Size=4014; Design=1903; Arrangement=781; % Width=90.0; Discharge=TAU,ROT CW,BOX 0; Rotation=CW; CFM=33109; SP=34.9 BHP; BHP=34.9; RPM=1775; Max Temp F=799; Effective Wheel Dia=42 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Wheel Material=CAST STEEL; Hub=19-5-219; Coupling=THOMAS 71 SIZE 300, BORE 2 3/16; Blades=10; Shaft Dia=4 7/16; Brg Centers=66 3/16; Critical Speed RPM=2839; STB=6.38; STH=2.50; Bearing Size=SIZE 2 3/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=326T; Drive=Direct | Open
408290 | HDX | CHECK VISION | pdf_vision | 408290 QT RUN REV 1.pdf |  |  | SN#408290 | 4014 | 1903 |  |  | 781 | 90.0 | TAU | CCW | 42 1/4 | 33709 | 3.4 | 34.9 | 1775 | 90 F | 799 | 0.0292 | 50.0 | 1800 | 19916 | 4 7/16 | 66 3/16 | 2839 |  |  |  | 6.38 |  | 2.50 | 2 3/16 | LINK BELT SERIES 6800 | 400000 | FIXED | 476 | FLOAT | 238 | 0 | 559 LB-FT2 | 2200 | 1045 STEEL | 0.15 | 0.25 |  |  | ASTM A1011-HSLAS | 0.105 (12) | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  |  | 10 | 2200 | 2820 | [10 empty] | 610 |  | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 8.510 |  | Included | 3.00 |  | 6007 | 121483 | 19-5-219 CAST STEEL | THOMAS 71 SIZE 300, BORE 2 3/16 | Direct | Required |  |  | Yes | Yes | [8 empty] | 2.1870 | 2.1860 |  | 0.5000 X 0.2500 | 73 | 15 1/2 | 789 |  | Yes | Ambient Temp F=90; Designer=JOHN ZINK | Size=4014; Design=1903; Arrangement=781; % Width=90.0; Discharge=TAU; Rotation=CCW; CFM=33709; SP=3.4; BHP=34.9; RPM=1775; Max Temp F=799; Effective Wheel Dia=42 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=19-5-219 CAST STEEL; Coupling=THOMAS 71 SIZE 300, BORE 2 3/16; Blades=10; Shaft Dia=4 7/16; Brg Centers=66 3/16; Critical Speed RPM=2839; STB=6.38; STH=2.50; Bearing Size=2 3/16; Bearing Series=LINK BELT SERIES 6800; Drive=Direct | Open
408294 | HD-PFD-IAF | OK | cbc_qt_run_text | QUOTE RUN.txt |  |  | 408294 | 3000 | 6105 |  |  | 1S | 100.0 | TH | CW | 31 1/2 | 16641 | 23.00 | 72.3 | 2484 | 140 | 140 | 0.0706 | 100.0 | 2484 | 20485 | 2 15/16 | 20 | 3657 | 43 11/16 | 11.76 | 17 1/4 | 12 | 84 | 1.94 | 2 15/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 1235 | FIXED | 259 | 166 | 155 | 2925 | 1045 STEEL | 0.17 | 0.50 |  |  | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 |  |  |  | 10 | 2954 | 5000 | [5 empty] | 6.2 | 3.0 |  |  |  |  | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 4.858 |  |  |  | Yes | 1331 | 26383 | 19-5-26 |  | Belt |  |  |  |  | Yes | [5 empty] | 2 15/16 | [10 empty] | Yes | Ambient Temp F=90 | Size=3000; Design=6105; Arrangement=1S; % Width=100.0; Discharge=TH; Rotation=CW; CFM=16641; SP=23.00; BHP=72.3; RPM=2484; Max Temp F=140; Effective Wheel Dia=31 1/2; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=19-5-26; Blades=10; Shaft Dia=2 15/16; Brg Centers=20; Critical Speed RPM=3657; BX=17 1/4; STB=12; OH=11.76; STH=1.94; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 6800; Drive=Belt | Open
408340 | GENERAL LINE | OK | cbc_qt_run_text | Quote Run - 408340.txt |  |  | 408340 | 18-1/4 | 36 | 1 |  | 9 | 100.0 | TH | CW |  | 1000 | 1.00 | 15.0 | 2706 | 70 | 70 | 0.0750 | 15.0 | 2706 | 13950 | 1 7/16 | 10 | 3598 | 25 3/4 | 7.87 | 12 | 5 3/4 |  | 1.86 | 1 7/16 | LINK BELT SERIES 200 | 23948 | FIXED | -278 | FIXED | 153 | 0 | 13 | 2997 | A240 304 SS | 0.29 | 0.48 |  |  | ASTM A240 304L SS | 0.060 (16) | ASTM A240 304L SS | 0.105 (12) | ASTM A240 304L SS | 0.105 (12) |  |  |  | 8 | 3141 | 9390 | [5 empty] | 5.6 | 3.0 | [13 empty] | 4-5-145 |  | Belt |  |  | Yes |  | Yes | [5 empty] | 1 7/16 | [11 empty] | Ambient Temp F=90 | Size=18-1/4; Design=36; Arrangement=9; % Width=100.0; Discharge=TH; Rotation=CW; Class=1; CFM=1000; SP=1.00; BHP=15.0; RPM=2706; Max Temp F=70; Blade Material=ASTM A240 304L SS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A240 304L SS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A240 304L SS; Backplate Gauge=0.105 (12); Hub=4-5-145; Blades=8; Shaft Dia=1 7/16; Brg Centers=10; Critical Speed RPM=3598; BX=12; STB=5 3/4; OH=7.87; STH=1.86; Bearing Size=1 7/16; Bearing Series=LINK BELT SERIES 200; Drive=Belt | Open
408355 | HDX | CHECK VISION | pdf_vision | QT RUN-408355.pdf |  |  | SN408355 | 3000 | 5800 |  | DISTRIBUTION AIR FAN; AB3030-1 | 48 | 100.0 | UB | CW | 29 | 7750 | 46.5 | 46.5 | 2960 | 100 | 100 | 0.0681 | 50.0 | 3000 | 22777 | [8 empty] | 1.38 | [15 empty] | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) |  |  | CAST STEEL | 10 | 4351 |  | 94 | 99 | 56 | 2.43 | 3.62 |  |  | 326TS |  | ODP | 800 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 1.172 |  | Not included |  | Included |  |  | 23-5-423 BORE 1 7/8 CAST STEEL |  | Motor mounted | Required |  |  |  | Yes | [5 empty] | 1 7/8 | [11 empty] | Ambient Temp F=90; Number of Blades=10; Wheel Weight=94; Thrust=99; WR2 Weight=56; Outlet Dimensions=12 IN. X 14 1/16 IN. (305 MM X 357 MM); Base=326TS; Motor=FR MOTOR; Frame=A36; Damper Frame=SKE-9-467 & -450; Damper Frame Thickness=1/4 PER SKE-9-449; Manual Control=OPERATING HANDLE LOC. 1, POS. 270; Good For=60 DAYS | Size=3000; Design=5800; Fan Type=DISTRIBUTION AIR FAN; AB3030-1; Arrangement=48; % Width=100.0; Discharge=UB; Rotation=CW; CFM=7750; SP=46.5; BHP=46.5; RPM=2960; Max Temp F=100; Effective Wheel Dia=29; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.135 (10); Wheel Material=CAST STEEL; Hub=23-5-423 BORE 1 7/8 CAST STEEL; Blades=10; STH=1.38; Motor Frame=326TS; Motor Enclosure=ODP; Drive=Motor mounted | Open
408398 | GENERAL LINE | OK | cbc_qt_run_text | quote run.txt |  |  | 408398 | 36 | A10 |  |  | 1S | 65.0 | BAU | CW |  | 1000 | 1.00 | 50.0 | 1800 | 180 | 180 | 0.0750 | 50.0 | 1800 | 18559 | 1 15/16 | 14 | 3176 | 30 11/16 | 8.12 | 16 15/16 | 5 1/4 | 26 | 3.44 | 1 15/16 | LINK BELT SERIES 200 | 400000 | FIXED | -57 | FIXED | 227 | 197 | 174 | 1847 | 1045 STEEL | 0.41 | 0.34 |  |  | ASTM A1008 HSLAS | 0.060 (16) | ASTM A1011 CS | 0.075 (14) | ASTM A1011 CS | 0.179 ( 7) |  |  |  | 8 | 2328 | 5280 | [11 empty] | 7 GA C.Q. HRS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 7.113 | [6 empty] | 4-5-15 | FALK G20 | Direct |  |  |  |  | Yes | [5 empty] | 1 15/16 | [10 empty] | Yes | Ambient Temp F=90 | Size=36; Design=A10; Arrangement=1S; % Width=65.0; Discharge=BAU; Rotation=CW; CFM=1000; SP=1.00; BHP=50.0; RPM=1800; Max Temp F=180; Blade Material=ASTM A1008 HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.075 (14); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.179 ( 7); Hub=4-5-15; Coupling=FALK G20; Blades=8; Shaft Dia=1 15/16; Brg Centers=14; Critical Speed RPM=3176; BX=16 15/16; STB=5 1/4; OH=8.12; STH=3.44; Bearing Size=1 15/16; Bearing Series=LINK BELT SERIES 200; Drive=Direct | Open
408656 | HD-PFD-IAF | OK | cbc_qt_run_text | 408656 QT RUN.docx |  |  | 408656 | 4014 | 1904 |  | PACKAGED FORCED DRAFT FAN | 8S | 90.0 | BH | CCW | 44 1/4 | 36299 | 16.50 | 132.2 | 1770 | 100 | 100 | 0.0670 | 150.0 | 1800 | 20864 | 2 15/16 | 14 | 4821 | 32 5/8 | 8.17 | 16 7/8 | 8 1/4 | 63 | 2.50 | 2 15/16 | LINK BELT SERIES 300 | 400000 | FIXED | -111 | FIXED | 514 | 292 | 509 | 2117 | 1045 STEEL | 0.30 | 0.27 | 26 3/4 |  | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 5/16 |  |  |  | 10 | 2130 | 2660 | [7 empty] | 445T |  |  | 1785 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 8.510 |  |  |  | Yes |  |  | 19-5-16 | FALK T10 | Direct |  |  |  |  | Yes | [5 empty] | 2 15/16 |  |  | 2.9370 | 2.9355 | 2.9375 | 0.7500 X 0.3750 |  |  |  |  | Yes | Ambient Temp F=100; Discharge Height (A)=45 13/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=30; Base Width (F)=55; Shaft Height (H)=50 13/16; Total Vert Height (TV)=83 11/16; Max Right of CL to Hsg (RH)=30; Max Left of CL to Disch (LH)=39 9/16; Base Flange to CL (D)=77 1/4; Drive End of Shaft to CL (K)=39 1/8; Mtg Flange to CL (LR)=16 3/8 | Size=4014; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=8S; % Width=90.0; Discharge=BH; Rotation=CCW; CFM=36299; SP=16.50; BHP=132.2; RPM=1770; Max Temp F=100; Effective Wheel Dia=44 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=5/16; Hub=19-5-16; Coupling=FALK T10; Blades=10; Shaft Dia=2 15/16; Brg Centers=14; Critical Speed RPM=4821; BX=16 7/8; STB=8 1/4; OH=8.17; STH=2.50; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 300; Housing Width (N)=26 3/4; Motor Frame=445T; Drive=Direct | Open
408682 | GENERAL LINE | OK | cbc_qt_run_text | 909-23-1168 - Wheel QT Run Rev1.txt |  |  | 408682 | 27 | B10 |  |  | 9H | 100.0 | UB | CW |  | 15920 | 14.00 | 48.4 | 2132 | 70 | 70 | 0.0750 | 75.0 | 2132 | 16261 | 2 11/16 | 13 | 5748 | 36 5/16 | 11.44 | 18 9/16 | 11 1/8 | 58 | 2.62 | 2 11/16 | LINK BELT SERIES 6800 | 400000 | FIXED | 954 | FIXED | 271 | 86 | 32 | 2277 | 1045 STEEL | 0.15 | 0.44 |  |  | ALUM 5052-H32 | 0.250 | ALUM 3003-O | 0.125 | ALUM 5052-H32 | 0.190 |  |  |  | 8 | 2277 | 3340 | [5 empty] | 7.2 | 3.0 | 365T | W |  | 920 | 10 GA C.Q. HRS | SK-9-236 MED PRESSURE, 30 IN. CENTERS | 4.350 | [6 empty] | 19-5-26 |  | Belt |  |  |  |  | Yes | [5 empty] | 2 11/16 | [10 empty] | Yes | Ambient Temp F=90 | Size=27; Design=B10; Arrangement=9H; % Width=100.0; Discharge=UB; Rotation=CW; CFM=15920; SP=14.00; BHP=48.4; RPM=2132; Max Temp F=70; Blade Material=ALUM 5052-H32; Blade Gauge=0.250; Sideplate Material=ALUM 3003-O; Sideplate Gauge=0.125; Backplate Material=ALUM 5052-H32; Backplate Gauge=0.190; Hub=19-5-26; Blades=8; Shaft Dia=2 11/16; Brg Centers=13; Critical Speed RPM=5748; BX=18 9/16; STB=11 1/8; OH=11.44; STH=2.62; Bearing Size=2 11/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=365T; Motor Position=W; Drive=Belt | Open
408682 | GENERAL LINE | OK | cbc_qt_run_text | 909-23-1168 -Shaft & Brg QT Run Rev1 (1).txt |  |  | 408682 | 300 | 51A | 3 |  | 9 |  |  |  |  | 15920 | 14.00 | 48.4 | 2132 |  |  |  |  | 2277 |  | 2 11/16 | 14 | 7187 | 36 7/8 | 9.03 | 15 7/8 | 11 1/8 | 59 | 0.00 | 2 11/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 764 | FIXED | 197 | 94 | 32 | 2277 | 1045 STEEL | 0.15 | 0.37 | [19 empty] | 9.0 | 3.0 | 365T | W |  | 920 | [11 empty] | Belt | Required |  |  |  | Yes | [5 empty] | 2 11/16 | [11 empty] | Ambient Temp F=90 | Size=300; Design=51A; Arrangement=9; Class=3; CFM=15920; SP=14.00; BHP=48.4; RPM=2132; Shaft Dia=2 11/16; Brg Centers=14; Critical Speed RPM=7187; BX=15 7/8; STB=11 1/8; OH=9.03; STH=0.00; Bearing Size=2 11/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=365T; Motor Position=W; Drive=Belt | Open
408800 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 408800 | 3000 | 6100 |  |  | 4S | 75.0 | UB | CW |  | 24000 | 24.00 | 131.7 | 3550 | 70 | 70 | 0.0694 | 150.0 | 3600 | 28274 | [8 empty] | 1.94 | [15 empty] | ASTM A6 XF-100 | 3/16 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 |  |  |  | 10 | 3822 | 6800 | 155 | 291 | 131 | 3.99 | 4.19 |  |  | 445TS |  |  | 1785 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 19 IN. CENTERS | 4.443 |  | Not included |  | Included | 3142 | 25594 | 19-5-27 |  | Motor mounted |  |  | Yes |  | Yes | [5 empty] | 2 3/8 | [11 empty] | Ambient Temp F=70 | Size=3000; Design=6100; Arrangement=4S; % Width=75.0; Discharge=UB; Rotation=CW; CFM=24000; SP=24.00; BHP=131.7; RPM=3550; Max Temp F=70; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=19-5-27; Blades=10; STH=1.94; Motor Frame=445TS; Drive=Motor mounted | Open
408831 | HDX | OK | pdf_vision | QT RUN.pdf |  |  | SN408831 | 4014 | 5800 |  |  | 4S | 100.0 | DB | CW | 42 1/2 | 12104 | 20.20 | 60.6 | 1770 | 100 | 130 | 0.0675 | 75.0 | 1800 | 20028 | 1 11/16 | 14 | 2770 | 27 3/16 | 6.47 | 11 1/8 | 5 1/2 | 17 | 2.00 | 1 11/16 | LINK BELT SERIES 300 | 400000 | FIXED | -63 | FIXED | 275 | 140 | 267 | 2042 | 1045 STEEL | 0.83 | 0.75 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 (7) |  |  | CAST STEEL | 10 | 3017 | [8 empty] | 365T |  |  | 920 | [9 empty] | 23-5-423 | FAIK G20, SIZE 1015G, BORE 1.688 | 365T FR MOTOR |  |  |  |  | Yes | [5 empty] | 1 11/16 |  |  | 1.6870 | 1.6860 | 1.6875 | 0.3750 X 0.1875 | [5 empty] | Ambient Temp F=70 | Size=4014; Design=5800; Arrangement=4S; % Width=100.0; Discharge=DB; Rotation=CW; CFM=12104; SP=20.20; BHP=60.6; RPM=1770; Max Temp F=130; Effective Wheel Dia=42 1/2; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 (7); Wheel Material=CAST STEEL; Hub=23-5-423; Coupling=FAIK G20, SIZE 1015G, BORE 1.688; Blades=10; Shaft Dia=1 11/16; Brg Centers=14; Critical Speed RPM=2770; BX=11 1/8; STB=5 1/2; OH=6.47; STH=2.00; Bearing Size=1 11/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=365T; Drive=365T FR MOTOR | Open
408832 | HDX | OK | pdf_vision | QT RUN.pdf |  |  | SN408831 | 4014 | 5800 |  |  | 4S | 100.0 | DB | CW | 42 1/2 | 12104 | 20.20 | 60.6 | 1770 | 100 | 130 | 0.0675 | 75.0 | 1800 | 20028 | 1 11/16 | 14 | 2770 | 27 3/16 | 6.47 | 11 1/8 | 5 1/2 | 17 | 2.00 | 1 11/16 | LINK BELT SERIES 300 | 68486 | FIXED | -63 | FIXED | 275 | 140 |  | 2042 |  | 0.83 | 0.75 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  | CAST STEEL | 10 | 3017 |  | 184 | 140 | 267 | 3.47 | 4.20 |  |  | 365T |  |  | 920 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 2.130 |  | Not included |  | Included | 2492 | 38599 | 23-5-423 | FAIK G20 | Direct |  |  |  |  | Yes | [5 empty] | 1 11/16 |  |  | 1.6870 | 1.6860 | 1.6875 | 0.3750 X 0.1875 | [5 empty] | Ambient Temp F=70 | Size=4014; Design=5800; Arrangement=4S; % Width=100.0; Discharge=DB; Rotation=CW; CFM=12104; SP=20.20; BHP=60.6; RPM=1770; Max Temp F=130; Effective Wheel Dia=42 1/2; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Wheel Material=CAST STEEL; Hub=23-5-423; Coupling=FAIK G20; Blades=10; Shaft Dia=1 11/16; Brg Centers=14; Critical Speed RPM=2770; BX=11 1/8; STB=5 1/2; OH=6.47; STH=2.00; Bearing Size=1 11/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=365T; Drive=Direct | Open
408888 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.docx |  |  | 408888 | 13 | 16A | 3 |  | 8S | 100.0 | BAU | CW | 22 5/8 | 1109 | 4.93 | 5.0 | 1755 | 550 | 550 | 0.0750 | 5.0 | 1755 |  | 1 11/16 | 16 | 3262 | 32 3/4 | 9.59 | 9 9/16 | 5 1/2 | 21 |  | 1 11/16 | LINK BELT SERIES 200 | 400000 | FIXED | -8 | FIXED | 77 | 0 | 12 | 2520 | 1045 STEEL | 0.15 | 0.06 | [10 empty] | A569 HRS | 6 | 2520 | [22 empty] | FALK T10 | Direct | Required |  |  |  | Yes | [5 empty] | 1 11/16 | [11 empty] | Ambient Temp F=90 | Size=13; Design=16A; Arrangement=8S; % Width=100.0; Discharge=BAU; Rotation=CW; Class=3; CFM=1109; SP=4.93; BHP=5.0; RPM=1755; Max Temp F=550; Effective Wheel Dia=22 5/8; Wheel Material=A569 HRS; Coupling=FALK T10; Blades=6; Shaft Dia=1 11/16; Brg Centers=16; Critical Speed RPM=3262; BX=9 9/16; STB=5 1/2; OH=9.59; Bearing Size=1 11/16; Bearing Series=LINK BELT SERIES 200; Drive=Direct | Open
408892 | HD-PFD-IAF | OK | cbc_qt_run_text | qt run.txt |  |  | 408892 | 2700 | 1903 |  | PACKAGED FORCED DRAFT FAN | 4S | 100.0 | DB | CW | 28 3/8 | 19000 | 23.61 | 125.0 | 3550 | 125 | 125 | 0.0750 | 125.0 | 3550 | 26348 | [8 empty] | 1.69 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A572 X-TEN | 1/4 |  |  |  | 10 | 4010 |  | 132 | 201 | 86 | 3.80 | 3.94 |  |  | 444TS |  |  | 1515 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 3.951 |  | Not included |  | Yes |  |  | 19-5-27 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 3/8 | [11 empty] | Ambient Temp F=90 | Size=2700; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S; % Width=100.0; Discharge=DB; Rotation=CW; CFM=19000; SP=23.61; BHP=125.0; RPM=3550; Max Temp F=125; Effective Wheel Dia=28 3/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 ( 7); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=19-5-27; Blades=10; STH=1.69; Motor Frame=444TS; Drive=Motor mounted | Open
408962 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 408962 | 2412 | 6195 |  |  | 4S | 85.0 | UB | CW | 23 1/4 | 14000 | 10.00 | 38.8 | 3500 | 70 | 70 | 0.0750 | 40.0 | 3600 | 24130 | [8 empty] | 1.62 | [15 empty] | ASTM A6 XF-100 | 3/16 | ASTM A572 X-TEN | 3/16 | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 10 | 4587 | 7340 | 92 | 108 | 51 | 3.41 | 4.12 |  |  | 324TS |  |  | 550 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 3.104 |  | Not included |  | Yes |  |  | 19-5-1056 |  | Motor mounted |  |  | Yes |  | Yes | [7 empty] | Q2 BUSHING 1 7/8 | [9 empty] | Ambient Temp F=70 | Size=2412; Design=6195; Arrangement=4S; % Width=85.0; Discharge=UB; Rotation=CW; CFM=14000; SP=10.00; BHP=38.8; RPM=3500; Max Temp F=70; Effective Wheel Dia=23 1/4; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=3/16; Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=19-5-1056; Blades=10; STH=1.62; Motor Frame=324TS; Drive=Motor mounted | Open
409095 | GENERAL LINE | OK | cbc_qt_run_text | 409095 QT RUN.txt |  |  | 409095 | 60 | A10 | 2 |  | 3D | 100.0 | TH | CCW |  | 35698 | 2.50 | 50.0 | 476 | 70 | 70 | 0.0750 | 50.0 | 476 | 8068 | 4 15/16 | 115 | 758 |  |  |  | 5.62 |  |  | 2 7/16 | LINK BELT SERIES 200 | 25920 | FIXED | 976 | FIXED | 951 | 0 | 5103 | 632 | 1045 STEEL | 0.36 | 0.58 |  |  | ASTM A1011 CS | 0.105 (12) | ASTM A1011 CS | 0.105 (12) | [6 empty] | 1129 | 2990 | [11 empty] | 1/4 C.Q. HRS | SK-9-236 LOW PRESSURE, 36 IN. CENTERS | 37.688 |  |  |  |  | 7735 | 94298 | 19-5-21 | FALK G20 | Direct | [21 empty] | Yes | Ambient Temp F=90 | Size=60; Design=A10; Arrangement=3D; % Width=100.0; Discharge=TH; Rotation=CCW; Class=2; CFM=35698; SP=2.50; BHP=50.0; RPM=476; Max Temp F=70; Blade Material=ASTM A1011 CS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.105 (12); Hub=19-5-21; Coupling=FALK G20; Shaft Dia=4 15/16; Brg Centers=115; Critical Speed RPM=758; STB=5.62; Bearing Size=2 7/16; Bearing Series=LINK BELT SERIES 200; Drive=Direct | Open
409197 | HD-PFD-IAF | OK | pdf_vision | QT RUN 6-7-23.pdf |  |  | 409197 | 2214 | 1903 |  | PACKAGED FORCED DRAFT FAN | 4S | 100.0 | PCT | CW | 23 3/8 | 10655 | 17.00 | 40.4 | 3565 | 80 | 120 | 0.0750 | 50.0 | 3600 | 22019 | 1 1/8 | 22 | [6 empty] | 1.62 | [15 empty] | ASTM A1011-HSLAS | 0.048 (18) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  | C. IRON | 10 | 4530 | 5840 | 64 | 95 | 26 | 3.11 | 4.62 |  |  | 326T |  | TEFC | 762 | 10 GA.6C IBS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 2.709 |  | Not included |  | Yes |  |  | 19-5-1055, Q1 BUSHING 2 1/8 | 3.11 | Motor mounted |  |  |  |  | Yes | [7 empty] | Q1 BUSHING 2 1/8 | [9 empty] | Ambient Temp F=90; Wheel Weight=64 LB; Thrust=95 LB; Base=326T FR MOTOR; Outlet=15 3/8 IN. X 25 3/8 IN. | Size=2214; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S; % Width=100.0; Discharge=PCT; Rotation=CW; CFM=10655; SP=17.00; BHP=40.4; RPM=3565; Max Temp F=120; Effective Wheel Dia=23 3/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.048 (18); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Wheel Material=C. IRON; Hub=19-5-1055, Q1 BUSHING 2 1/8; Coupling=3.11; Blades=10; Shaft Dia=1 1/8; Brg Centers=22; STH=1.62; Motor Frame=326T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
409198 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 409198 | 30 | A10 |  |  | 4S | 100.0 | BAU | CW |  | 1000 | 1.00 | 30.0 | 1800 | 70 | 70 | 0.0750 | 30.0 | 1800 | 15254 | [8 empty] | 2.94 | [15 empty] | ASTM A1008 HSLAS | 0.060 (16) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A572 X-TEN | 3/8 |  |  |  | 12 | 2932 | 13850 | 171 | 90 | 157 | 5.13 | 7.88 |  |  | 286T |  | ODP | 390 | 10 GA C.Q. HRS | SK-9-236 MED PRESSURE, 30 IN. CENTERS | 5.394 |  | Not included |  |  |  |  | 4-5-15 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 1 7/8 | [11 empty] | Ambient Temp F=90 | Size=30; Design=A10; Arrangement=4S; % Width=100.0; Discharge=BAU; Rotation=CW; CFM=1000; SP=1.00; BHP=30.0; RPM=1800; Max Temp F=70; Blade Material=ASTM A1008 HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Hub=4-5-15; Blades=12; STH=2.94; Motor Frame=286T; Motor Enclosure=ODP; Drive=Motor mounted | Open
409261 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 409261 | 12 | 36 |  |  | 1S | 100.0 | TH | CCW |  | 1280 | 1.50 | 0.4 | 1679 | 70 | 70 | 0.0750 | 1.0 | 1679 | 5810 | [24 empty] | ALUM 5052-H32 | 0.125 | ALUM 3003-O | 0.125 | ALUM 5052-H32 | 0.125 |  |  |  | 12 | 4872 | 11670 | [9 empty] | TEFC | [35 empty] | Ambient Temp F=90 | Size=12; Design=36; Arrangement=1S; % Width=100.0; Discharge=TH; Rotation=CCW; CFM=1280; SP=1.50; BHP=0.4; RPM=1679; Max Temp F=70; Blade Material=ALUM 5052-H32; Blade Gauge=0.125; Sideplate Material=ALUM 3003-O; Sideplate Gauge=0.125; Backplate Material=ALUM 5052-H32; Backplate Gauge=0.125; Blades=12; Motor Enclosure=TEFC | Open
409278 | HD-PFD-IAF | OK | cbc_qt_run_text | 409278_253-23-370 - QT Run Rev1 (MIXING BOX).txt |  |  | 409278 | 4412 | 1904 |  | PACKAGED FORCED DRAFT FAN | 4S1 | 75.0 | DB | CW | 48 15/16 | 30680 | 26.17 | 159.6 | 1785 | 151 | 151 | 0.0640 | 200.0 | 1800 | 23067 | [8 empty] | 2.81 | [15 empty] | ASTM A1011-HSLAS | 0.060 (16) | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM CQ HRS A36 | 3/8 |  |  |  | 10 | 2109 | 2640 | 455 | 436 | 869 | 4.93 | 7.19 |  |  | 447T |  | TEFC | 2850 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 9.844 |  | Not included |  |  |  |  | 19-5-289 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 3 3/8 | [6 empty] | 80 | 17 | 315 |  |  | Ambient Temp F=70 | Size=4412; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S1; % Width=75.0; Discharge=DB; Rotation=CW; CFM=30680; SP=26.17; BHP=159.6; RPM=1785; Max Temp F=151; Effective Wheel Dia=48 15/16; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 ( 7); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=3/8; Hub=19-5-289; Blades=10; STH=2.81; Motor Frame=447T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
409372 | GENERAL LINE | OK | cbc_qt_run_text | 409372 QT RUN REVISED.txt |  |  | 409372 | 22 | A10 |  |  | 4S | 85.0 | TH | CW |  | 11000 | 24.53 | 51.0 | 3500 | 70 | 140 | 0.0750 | 60.0 | 3600 | 22627 | [8 empty] | 2.27 | [15 empty] | ASTM A1008 HSLAS | 0.048 (18) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011 CS | 0.179 ( 7) |  |  |  | 12 | 4409 | 11890 | 73 | 109 | 32 | 3.86 | 4.77 |  |  | 326T |  | ODP | 610 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 2.813 |  | Not included |  |  |  |  | 19-5-1056 |  | Motor mounted | Required |  |  |  | Yes | [7 empty] | Q2 BUSHING 1 7/8 | [9 empty] | Ambient Temp F=70 | Size=22; Design=A10; Arrangement=4S; % Width=85.0; Discharge=TH; Rotation=CW; CFM=11000; SP=24.53; BHP=51.0; RPM=3500; Max Temp F=140; Blade Material=ASTM A1008 HSLAS; Blade Gauge=0.048 (18); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.179 ( 7); Hub=19-5-1056; Blades=12; STH=2.27; Motor Frame=326T; Motor Enclosure=ODP; Drive=Motor mounted | Open
409401 | GENERAL LINE | OK | cbc_qt_run_text | 409401 QT RUN REVISED.txt |  |  | 409401 | 27 | A10 |  |  | 4S | 70.0 | BAU | CW |  | 1000 | 1.00 | 125.0 | 3550 | 70 | 140 | 0.0750 | 125.0 | 3600 | 27457 | [8 empty] | 2.62 | [15 empty] | ASTM A1008 HSLAS | 0.060 (16) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011 CS | 0.179 ( 7) |  |  |  | 12 | 4037 | 8250 | 108 | 236 | 72 | 4.27 | 4.88 |  |  | 444T |  |  | 1515 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 3.961 |  | Not included |  |  | 2653 | 19144 | 19-5-1057 |  | Motor mounted | Required |  |  |  | Yes | [7 empty] | Q2 BUSHING 2 3/8 | [9 empty] | Ambient Temp F=70 | Size=27; Design=A10; Arrangement=4S; % Width=70.0; Discharge=BAU; Rotation=CW; CFM=1000; SP=1.00; BHP=125.0; RPM=3550; Max Temp F=140; Blade Material=ASTM A1008 HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.179 ( 7); Hub=19-5-1057; Blades=12; STH=2.62; Motor Frame=444T; Drive=Motor mounted | Open
409419 | GENERAL LINE | OK | cbc_qt_run_text | 409419 QT RUN.txt |  |  | 409419 | 30 | 36 | 2 |  | 1S | 100.0 | TH | CW |  | 8000 | 0.60 | 1.6 | 580 | 70 | 70 | 0.0750 | 2.0 | 580 | 4915 |  |  | 2951 | [6 empty] | 2 3/16 | LINK BELT SERIES 200 | 400000 | FIXED | -54 | FIXED | 252 | 10 | [7 empty] | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011 CS | 0.179 ( 7) |  |  |  | 12 | 1788 | [6 empty] | 26.3 | 3.0 | [13 empty] | 4-5-15 |  | Belt |  |  |  |  | Yes | [5 empty] | 2 3/16 | [11 empty] | Ambient Temp F=70 | Size=30; Design=36; Arrangement=1S; % Width=100.0; Discharge=TH; Rotation=CW; Class=2; CFM=8000; SP=0.60; BHP=1.6; RPM=580; Max Temp F=70; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.179 ( 7); Hub=4-5-15; Blades=12; Critical Speed RPM=2951; Bearing Size=2 3/16; Bearing Series=LINK BELT SERIES 200; Drive=Belt | Open
409440 | HD-PFD-IAF | CHECK VISION | pdf_vision | QT RUN-CO#3.pdf |  |  | SN#409440 | 3000 | 5800 |  |  | 4S1 | 100.0 | BH | CW | 31 3/4 | 1158 CPM | 40.26 | 112.8 | 3534 | 100 | 100 | 0.0635 | 125.0 | 3600 | 29924 | 1 15/16 | 12 | 5528 | 25 9/16 | 5.92 | 9 7/16 | 6 |  | 1.38 | 1 15/16 | Link Belt Series 6800 | 400000 | FIXED | -18 | FLOAT | 163 | 0 | 77 | 4076 |  | 0.63 | 0.40 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) |  |  | CAST STEEL | 10 | 4076 |  | 107 | 174 | 77 | 2.49 | 3.62 |  |  | 444TS |  |  | 1515 | 1/4 C.Q. HRS |  |  |  | Not included |  |  | 3063 | 32968 | 23-5-423 | Falk G20, Size 1020G | TS FRAME MOTOR | Required | Required |  | Yes | Yes | [5 empty] | 2 3/8 |  |  | 1.9370 | 1.9360 | 1.9375 | 0.5000 X 0.2500 | 41 | 12 7/8 | 1 |  |  | Ambient Temp F=32 | Size=3000; Design=5800; Arrangement=4S1; % Width=100.0; Discharge=BH; Rotation=CW; CFM=1158 CPM; SP=40.26; BHP=112.8; RPM=3534; Max Temp F=100; Effective Wheel Dia=31 3/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.135 (10); Wheel Material=CAST STEEL; Hub=23-5-423; Coupling=Falk G20, Size 1020G; Blades=10; Shaft Dia=1 15/16; Brg Centers=12; Critical Speed RPM=5528; BX=9 7/16; STB=6; OH=5.92; STH=1.38; Bearing Size=1 15/16; Bearing Series=Link Belt Series 6800; Motor Frame=444TS; Drive=TS FRAME MOTOR | Open
409519 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 409519 | 135 | 51A | 1 |  | 3 |  |  |  |  | 1000 | 1.00 | 3.0 | 1000 |  |  |  |  | 5288 | 3461 | 1 3/16 | 14 | 6666 |  |  |  | 5.90 | 7 | 1.19 | 1 3/16 | LINK BELT SERIES 200 | 400000 | FIXED | 69 | FIXED | 7 | 0 | 2 | 5288 | 1045 STEEL | 0.51 | 0.56 |  |  | ASTM A1008 HSLAS | 0.048 (18) | ASTM A1011 CS | 0.048 (18) | ASTM A1011 CS | 0.075 (14) |  |  |  | 8 | 5288 | 15600 | [5 empty] | 19.1 | [14 empty] | 4-5-16 |  | Belt | [10 empty] | 1 3/16 | [11 empty] | Ambient Temp F=90 | Size=135; Design=51A; Arrangement=3; Class=1; CFM=1000; SP=1.00; BHP=3.0; RPM=1000; Blade Material=ASTM A1008 HSLAS; Blade Gauge=0.048 (18); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.048 (18); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.075 (14); Hub=4-5-16; Blades=8; Shaft Dia=1 3/16; Brg Centers=14; Critical Speed RPM=6666; STB=5.90; STH=1.19; Bearing Size=1 3/16; Bearing Series=LINK BELT SERIES 200; Drive=Belt | Open
409735 | GENERAL LINE | OK | cbc_qt_run_text | 409735_QT Run-AWS WELD AND DYE PEN.txt |  |  | 409735 | 2400 | 2302B |  |  | 8S | 100.0 | UB | CW | 24 1/2 | 2108 | 13.53 | 6.1 | 2931 | 752 | 752 | 0.0308 | 20.0 | 3000 | 19227 | 2 3/16 | 10 | 4495 | 25 1/16 | 8.43 | 9 3/8 | 5 1/2 |  | 1.25 | 2 3/16 | LINK BELT SERIES 300 | 400000 | FIXED | -71 | FIXED | 222 | 84 | 51 | 3596 | 1045 STEEL | 0.26 | 0.06 |  |  | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 |  |  |  | 11 | 4159 | 10620 | [7 empty] | 256T |  | TEFC | 312 | 10 GA A607 X-TEN | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 0.641 |  |  |  |  | 1042 | 44514 | 23-5-423 | FALK G20 | Direct |  |  |  | Yes | Yes | [5 empty] | 1 15/16 | [10 empty] | Yes | Ambient Temp F=40 | Size=2400; Design=2302B; Arrangement=8S; % Width=100.0; Discharge=UB; Rotation=CW; CFM=2108; SP=13.53; BHP=6.1; RPM=2931; Max Temp F=752; Effective Wheel Dia=24 1/2; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=23-5-423; Coupling=FALK G20; Blades=11; Shaft Dia=2 3/16; Brg Centers=10; Critical Speed RPM=4495; BX=9 3/8; STB=5 1/2; OH=8.43; STH=1.25; Bearing Size=2 3/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=256T; Motor Enclosure=TEFC; Drive=Direct | Open
409784 | HD-PFD-IAF | CHECK VISION | pdf_vision | 409784_QT RUN-GMH.pdf |  |  | POWER FLAME D1902 | 3000 | 1902 |  | PACKAGED FORCED DRAFT FAN | 4S | 95.0 | DISCH BAU, ROT CW | CW | 26704 RE SK-9-105 | 20000 | 5.0 IN. | 144.2 | 3400 | 70 | 70 | 0.0750 | 150.0 | 4400 | 26704 | Thrust 244 LB, WR2 165 LB-FT2 | [7 empty] | 1.94 | 184 LB | [14 empty] | ASTM A1011-HSLAS | 0 IPS (12) | ASTM A572 X-TEN | 1/4 | ASTM A-TEN | 5/16 |  |  | C. IRON | 10 | 3481 | 5070 | 184 | 244 | 165 | 4.40 | 4.44 |  |  | 444TS |  |  | 1515 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 4.769 |  | Not included |  | Yes | 2760 | 19948 | 19-5-1056, Q2 BUSHING 2 3/8 |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q2 BUSHING 2 3/8 | [9 empty] | Ambient Temp F=70; Outlet=20 1/8 IN. X 34 1/8 IN., 511 MM X 867 MM; Base=444TS FR MOTOR; Housing=10 GA C.Q. HRS | Size=3000; Design=1902; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S; % Width=95.0; Discharge=DISCH BAU, ROT CW; Rotation=CW; CFM=20000; SP=5.0 IN.; BHP=144.2; RPM=3400; Max Temp F=70; Effective Wheel Dia=26704 RE SK-9-105; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0 IPS (12); Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A-TEN; Backplate Gauge=5/16; Wheel Material=C. IRON; Hub=19-5-1056, Q2 BUSHING 2 3/8; Blades=10; Shaft Dia=Thrust 244 LB, WR2 165 LB-FT2; STH=1.94; Bearing Size=184 LB; Motor Frame=444TS; Drive=Motor mounted | Open
409819 | GENERAL LINE | OK | d64_wheel_construction | 409819_D64 Wheel Construction (Outer Ring) 345-20-1754.xlsx | [103 empty] | Fan Size=182; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=50000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.25 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=182; Outer Ring Thickness=0.25; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=50000 | Open
409831 | HD-PFD-IAF | OK | cbc_qt_run_text | FA DAMPER QT RUN.txt | DAMPER |  | 409831 | 4014 | 1904 |  | PACKAGED FORCED DRAFT FAN | 4S1 | 80.0 | DB | CW | 44 1/4 | 26214 | 20.47 | 109.9 | 1770 | 108 | 137 | 0.0682 | 125.0 | 1800 | 20864 | [8 empty] | 2.50 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 5/16 |  |  |  | 10 | 2168 | 2710 | 303 | 292 | 492 | 4.41 | 6.38 |  |  | 444T |  |  | 1515 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 8.192 |  | Not included |  |  |  |  | 19-5-16 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 3 3/8 | [6 empty] | 73 | 15 9/16 | 1 |  |  | Ambient Temp F=90 | Size=4014; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S1; % Width=80.0; Discharge=DB; Rotation=CW; CFM=26214; SP=20.47; BHP=109.9; RPM=1770; Max Temp F=137; Effective Wheel Dia=44 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=5/16; Hub=19-5-16; Blades=10; STH=2.50; Motor Frame=444T; Drive=Motor mounted | Open
409831 | HD-PFD-IAF | OK | cbc_qt_run_text | IVC QT RUN.txt |  |  | 409831 | 4014 | 1904 |  | PACKAGED FORCED DRAFT FAN | 4S | 80.0 | DB | CW | 44 1/4 | 26214 | 20.47 | 109.9 | 1770 | 108 | 137 | 0.0682 | 125.0 | 1800 | 20864 | [8 empty] | 2.50 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 5/16 |  |  |  | 10 | 2168 | 2710 | 303 | 292 | 492 | 4.41 | 6.38 |  |  | 444T |  |  | 1515 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 8.192 |  | Not included |  | Yes |  |  | 19-5-16 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 3 3/8 | [9 empty] | SK-19-72 |  | Ambient Temp F=90 | Size=4014; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S; % Width=80.0; Discharge=DB; Rotation=CW; CFM=26214; SP=20.47; BHP=109.9; RPM=1770; Max Temp F=137; Effective Wheel Dia=44 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=5/16; Hub=19-5-16; Blades=10; STH=2.50; Motor Frame=444T; Drive=Motor mounted | Open
409832 | HD-PFD-IAF | OK | cbc_qt_run_text | Access 223192 - 1997 RPM Wheel QT Run.txt |  |  | 409832 | 4014 | 1903 |  | PACKAGED FORCED DRAFT FAN | 4S | 50.0 | BAU | CW | 42 1/4 | 16500 | 22.00 | 76.4 | 1997 | 120 | 120 | 0.0629 | 100.0 | 2000 | 22129 | [8 empty] | 2.50 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 1/4 |  |  |  | 10 | 2278 | 2850 | 231 | 315 | 305 | 3.80 | 7.25 |  |  | 404T |  | ODP | 1145 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 7.278 |  | Not included |  | Yes |  |  | 19-5-16 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 7/8 | [11 empty] | Ambient Temp F=70 | Size=4014; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S; % Width=50.0; Discharge=BAU; Rotation=CW; CFM=16500; SP=22.00; BHP=76.4; RPM=1997; Max Temp F=120; Effective Wheel Dia=42 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Hub=19-5-16; Blades=10; STH=2.50; Motor Frame=404T; Motor Enclosure=ODP; Drive=Motor mounted | Open
409960 | HDX | CHECK VISION | pdf_vision | 19674D ARGENTINA QT RUN-07112018081709 PD - LARRY PARA FABRICAR.PDF |  |  | 19674D VTI-LJL | 10300 | 1903 |  |  | IS | 100.0 | UB | CW | 108 1/8 | 139400 | 9.48 | 786 | 959 | 230 | 230 | 0.640 | 1000 | 1100 | 31145 | 8 | 26 | 1812 | 74 1/4 | 25.86 | 49 3/16 | 17 3/16 |  | 5.44 | 8 | LINK BELT SERIES 6800 | 400000 | FIXED | -4319 | FLOAT | 10936 | 0 | 45171 | 1165 | 1045 STEEL | 0.44 | 0.25 |  |  | ASTM A6 XF-100 | 3/16 | ASTM A6 XF-100 | 5/16 | ASTM A572 X-TEN | 3/4 |  |  |  |  | 1165 | [16 empty] | Included | 2.00 |  |  |  | 19-5-1885 BORE 7 3/4 CAST STEEL | FALK T31, SIZE 1140T, BORE 7.500 NOT INCL. | Direct |  | Required | Yes | Yes | [6 empty] | 7 3/4 | [11 empty] | Ambient Temp F=35 | Size=10300; Design=1903; Arrangement=IS; % Width=100.0; Discharge=UB; Rotation=CW; CFM=139400; SP=9.48; BHP=786; RPM=959; Max Temp F=230; Effective Wheel Dia=108 1/8; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=5/16; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/4; Hub=19-5-1885 BORE 7 3/4 CAST STEEL; Coupling=FALK T31, SIZE 1140T, BORE 7.500 NOT INCL.; Shaft Dia=8; Brg Centers=26; Critical Speed RPM=1812; BX=49 3/16; STB=17 3/16; OH=25.86; STH=5.44; Bearing Size=8; Bearing Series=LINK BELT SERIES 6800; Drive=Direct | Open
410038 | GENERAL LINE | OK | cbc_qt_run_text | 410038_350-16-1173 wheel quote run.txt |  |  | 410038 | 222 | 51A | 3 |  | 3 |  |  |  |  | 0 | 0.00 | 5.0 | 1800 |  |  |  |  | 2135 | 10161 | 1 11/16 | 34 | 2562 |  |  |  | 4.80 | 26 |  | 1 11/16 | LINK BELT SERIES 200 | 400000 | FIXED | 52 | FIXED | 44 | 0 | 30 | 2135 | 1045 STEEL | 0.14 | 0.05 |  |  | ASTM A240 304L SS | 0.060 (16) | ASTM A240 304L SS | 0.105 (12) | [6 empty] | 3694 | 4430 | [20 empty] | 4-5-145 | FALK G20 | Direct | Required | [22 empty] | Size=222; Design=51A; Arrangement=3; Class=3; CFM=0; SP=0.00; BHP=5.0; RPM=1800; Blade Material=ASTM A240 304L SS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A240 304L SS; Sideplate Gauge=0.105 (12); Hub=4-5-145; Coupling=FALK G20; Shaft Dia=1 11/16; Brg Centers=34; Critical Speed RPM=2562; STB=4.80; Bearing Size=1 11/16; Bearing Series=LINK BELT SERIES 200; Drive=Direct | Open
410087 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 410087 | 4900 | 6195 |  |  | 8S1 | 100.0 | BAU | CW | 46 9/16 | 60000 | 16.00 | 211.7 | 1770 | 70 | 70 | 0.0750 | 250.0 | 1800 | 24130 | 3 7/16 | 16 | 3279 | 38 1/4 | 11.17 | 21 3/8 | 9 7/8 |  | 2.94 | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -291 | FLOAT | 1022 | 0 | 1285 | 2109 | 1045 STEEL | 0.41 | 0.28 | 33 5/8 |  | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 3/8 |  |  |  | 10 | 2109 | 3030 | [7 empty] | 449T |  |  | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 13.033 | 54.250 | Included |  |  | 11085 | 97672 | 19-5-219 | FALK T10 | Direct |  |  | Yes | Yes | Yes | [5 empty] | 3 3/16 |  |  | 3.4370 | 3.4355 | 3.4375 | 0.8750 X 0.4375 | 98 | 20 3/4 | 1 | SK-19-72 | Yes | Ambient Temp F=70; Discharge Height (A)=55 13/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=79 3/8; Base Width (F)=66 1/4; Inlet Box Width (B)=98; Inlet Box Length To Cl (J)=60 1/2; Shaft Height (H)=58 11/16; Total Vert Height (TV)=119 3/16; Max Right of CL to Hsg (RH)=51; Max Left of CL to Disch (LH)=97; Base Flange to CL (D)=93 7/8; Drive End of Shaft to CL (K)=47 1/4; Box Cl To Hsg Cl (P)=26 15/16; Box Width Os (C)=20 3/4; Mtg Flange to CL (LR)=40 5/16 | Size=4900; Design=6195; Arrangement=8S1; % Width=100.0; Discharge=BAU; Rotation=CW; CFM=60000; SP=16.00; BHP=211.7; RPM=1770; Max Temp F=70; Effective Wheel Dia=46 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Hub=19-5-219; Coupling=FALK T10; Blades=10; Shaft Dia=3 7/16; Brg Centers=16; Critical Speed RPM=3279; BX=21 3/8; STB=9 7/8; OH=11.17; STH=2.94; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=33 5/8; Motor Frame=449T; Drive=Direct | Open
410088 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 410088 | 4900 | 6195 |  |  | 8S1 | 100.0 | TAU | CW | 46 9/16 | 60000 | 16.00 | 211.7 | 1770 | 70 | 70 | 0.0750 | 250.0 | 1800 | 21936 | 3 7/16 | 16 | 3250 | 38 1/4 | 11.30 | 21 3/8 | 9 7/8 |  | 2.94 | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -291 | FLOAT | 1016 | 0 | 1268 | 2070 | 1045 STEEL | 0.41 | 0.28 | 33 5/8 |  | ASTM A6 XF-100 | 1/4 | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 3/8 |  |  |  | 10 | 2070 | 3030 | [7 empty] | 449T |  |  | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 13.033 | 54.250 |  |  |  | 10703 | 108398 | 19-5-289 | FALK T10 | Direct |  |  | Yes | Yes | Yes | [5 empty] | 3 3/16 |  |  | 3.4370 | 3.4355 | 3.4375 | 0.8750 X 0.4375 | 98 | 20 3/4 | 1 | SK-19-72 | Yes | Ambient Temp F=70; Discharge Height (A)=55 13/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=72 3/8; Base Width (F)=66 1/4; Inlet Box Width (B)=98; Inlet Box Length To Cl (J)=49 3/4; Shaft Height (H)=50 1/2; Total Vert Height (TV)=142 9/16; Max Right of CL to Hsg (RH)=52 9/16; Max Left of CL to Disch (LH)=52 3/16; Base Flange to CL (D)=93 7/8; Drive End of Shaft to CL (K)=47 1/4; Box Cl To Hsg Cl (P)=40 11/16; Box Width Os (C)=20 3/4; Mtg Flange to CL (LR)=54 1/16 | Size=4900; Design=6195; Arrangement=8S1; % Width=100.0; Discharge=TAU; Rotation=CW; CFM=60000; SP=16.00; BHP=211.7; RPM=1770; Max Temp F=70; Effective Wheel Dia=46 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Hub=19-5-289; Coupling=FALK T10; Blades=10; Shaft Dia=3 7/16; Brg Centers=16; Critical Speed RPM=3250; BX=21 3/8; STB=9 7/8; OH=11.30; STH=2.94; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=33 5/8; Motor Frame=449T; Drive=Direct | Open
410089 | HDX | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | SN#410089 | 2700 | 1911 |  |  | 48 | 100.0 | DB | CW | 29 1/8 | 28050 | 19.86 | 125.0 | 3573 | 70 | 155 | 0.0590 | 125.0 | 3600 | 27450 | 2 7/16 | 14 | 4544 | 29 3/4 | 9.48 | 15 3/4 | 6 1/2 |  | 2.62 | 2 7/16 | S800 | 19 | FIXED | -39 | FLOAT | 215 | 0 | 83 | 3634 | 1045 STEEL | 0.32 | 0.21 |  |  | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.179 (7) | ASTM A1011-HSLAS | 0.179 (7) |  |  | CAST STEEL | 8 | 3719 | 4690 | 123 | 269 | 88 | 5.42 | 4.88 |  |  | 444TS |  |  | 1515 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS |  |  | Not included |  | Included |  |  | 19-5-27 | FALK G20, SIZE 1020G | Motor mounted | Required | Required |  | Yes | Yes | [5 empty] | 2 3/16 |  | Q2 BUSHING 2 3/8 | 2.4370 | 2.4360 | 2.4375 | 0.6250 X 0.3125 |  |  |  | SK-19-72 |  | Ambient Temp F=70 | Size=2700; Design=1911; Arrangement=48; % Width=100.0; Discharge=DB; Rotation=CW; CFM=28050; SP=19.86; BHP=125.0; RPM=3573; Max Temp F=155; Effective Wheel Dia=29 1/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 (7); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 (7); Wheel Material=CAST STEEL; Hub=19-5-27; Coupling=FALK G20, SIZE 1020G; Blades=8; Shaft Dia=2 7/16; Brg Centers=14; Critical Speed RPM=4544; BX=15 3/4; STB=6 1/2; OH=9.48; STH=2.62; Bearing Size=2 7/16; Bearing Series=S800; Motor Frame=444TS; Drive=Motor mounted | Open
410149 | GENERAL LINE | OK | cbc_qt_run_text | 410149 QT RUN.txt |  |  | 410149 | 222 | 51A | 1 |  | 3 |  |  |  |  | 10000 | 5.00 | 16.9 | 2150 |  |  |  |  | 2719 | 12137 | 1 15/16 | 35 | 3264 |  |  |  | 7.50 | 40 |  | 1 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | 243 | FLOAT | 29 | 0 | 20 | 2719 | 1045 STEEL | 0.10 | 0.20 |  |  | ASTM A1008 HSLAS | 0.048 (18) | ASTM A1011 CS | 0.060 (16) | [6 empty] | 3225 | 5110 | [5 empty] | 8.9 | [14 empty] | 4-5-38 |  | Belt | Required | [9 empty] | 1 15/16 | [12 empty] | Size=222; Design=51A; Arrangement=3; Class=1; CFM=10000; SP=5.00; BHP=16.9; RPM=2150; Blade Material=ASTM A1008 HSLAS; Blade Gauge=0.048 (18); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.060 (16); Hub=4-5-38; Shaft Dia=1 15/16; Brg Centers=35; Critical Speed RPM=3264; STB=7.50; Bearing Size=1 15/16; Bearing Series=LINK BELT SERIES 6800; Drive=Belt | Open
410181 | HDX | OK | pdf_vision | QT RUN-CO#3.pdf |  |  | SN410181 | 4412 | 5500 | ARK 7SL |  |  | 100.0 | DB | CW | 47 5/8 | 26493 | 25.60 | 137.2 | 1780 | 125 | 125 | 0.0627 | 150.0 | 1800 | 22443 | 7/16 | 43 5/8 | 2772 | 54.88 | 33.94 | 7.77 | 8.50 | 71 |  | 3 3/16 | Link Belt Series 6800 | 400000 | FIXED | 321 | FLOAT | 73 | 0 | 447 | 1979 |  | 0.51 | 0.68 |  |  | ASTM A1011-HSIAS | 0.135 (10) | ASTM A1011-HSIAS | 0.135 (10) | ASTM A1011-HSIAS | 0.179 (7) |  |  | CAST STEEL | 16 | 2626 | [11 empty] | 1753 | 1/4 C.O. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 5.184 |  |  |  |  | 6008 | 74288 | 2 3/16 | FALK T10, SIZE 1100T, BORE 2 3/16 | DRIVE-FIXED |  |  |  | Yes | Yes | [5 empty] | 2 7/16 |  |  | 2.1870 | 2.1860 |  | 0.5000 X 0.2500 | 60 3/4 | 19 1/8 | 789 |  | Yes | Ambient Temp F=70 | Size=4412; Design=5500; % Width=100.0; Discharge=DB; Rotation=CW; Class=ARK 7SL; CFM=26493; SP=25.60; BHP=137.2; RPM=1780; Max Temp F=125; Effective Wheel Dia=47 5/8; Blade Material=ASTM A1011-HSIAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSIAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSIAS; Backplate Gauge=0.179 (7); Wheel Material=CAST STEEL; Hub=2 3/16; Coupling=FALK T10, SIZE 1100T, BORE 2 3/16; Blades=16; Shaft Dia=7/16; Brg Centers=43 5/8; Critical Speed RPM=2772; BX=7.77; STB=8.50; OH=33.94; Bearing Size=3 3/16; Bearing Series=Link Belt Series 6800; Drive=DRIVE-FIXED | Open
410186 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN REVISED PER FEA.txt |  |  | 410186 | 5414 | 6195 |  |  | 8S | 75.0 | TAU | CW | 51 9/16 | 63214 | 20.70 | 272.1 | 1780 | 86 | 86 | 0.0720 | 300.0 | 1800 | 24287 | 4 3/16 | 14 | 3545 | 39 3/4 | 12.99 | 23 13/16 | 10 1/8 |  | 3.38 | 4 3/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -633 | FLOAT | 1689 | 0 | 2148 | 1900 | 1045 STEEL | 0.25 | 0.19 | 33 7/8 |  | ASTM A6 XF-100 | 5/16 | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 1/2 |  |  |  | 10 | 2233 | 4230 | [9 empty] | ODP | 3250 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 14.526 |  | Included |  | Yes | 9763 | 96346 | 19-5-12 | FALK T10 | Direct |  |  | Yes | [7 empty] | 4 3/16 |  |  | 4.1870 | 4.1855 | 4.1875 | 1.0000 X 0.5000 |  |  |  | SK-19-72 | Yes | Ambient Temp F=70; Discharge Height (A)=61 3/4; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=40 3/8; Base Width (F)=72 1/2; Shaft Height (H)=57 3/16; Total Vert Height (TV)=130 13/16; Max Right of CL to Hsg (RH)=39 5/8; Max Left of CL to Disch (LH)=57 11/16; Base Flange to CL (D)=94 7/8; Drive End of Shaft to CL (K)=47 15/16; Mtg Flange to CL (LR)=19 3/16 | Size=5414; Design=6195; Arrangement=8S; % Width=75.0; Discharge=TAU; Rotation=CW; CFM=63214; SP=20.70; BHP=272.1; RPM=1780; Max Temp F=86; Effective Wheel Dia=51 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=5/16; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Hub=19-5-12; Coupling=FALK T10; Blades=10; Shaft Dia=4 3/16; Brg Centers=14; Critical Speed RPM=3545; BX=23 13/16; STB=10 1/8; OH=12.99; STH=3.38; Bearing Size=4 3/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=33 7/8; Motor Enclosure=ODP; Drive=Direct | Open
410188 | GENERAL LINE | OK | cbc_qt_run_text | 410188 QT Run-Revised for 3.9375 shaft.txt |  |  | 410188 | 4900 | 6195 |  |  | 8S | 110.0 | DB | CCW | 46 9/16 | 70630 | 11.86 | 215.2 | 1780 | 86 | 103 | 0.0716 | 250.0 | 1800 | 21936 | 3 15/16 | 14 | 3360 | 38 9/16 | 14.00 | 24 1/4 | 9 7/8 | 133 | 2.94 | 3 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -468 | FLOAT | 1239 | 0 | 1308 | 1878 | 1045 STEEL | 0.25 | 0.19 | 34 3/4 |  | ASTM A6 XF-100 | 1/4 | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 3/8 |  |  |  | 10 | 1878 | 2760 | [9 empty] | ODP | 3250 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 13.469 |  | Included |  | Yes | 8407 | 77702 | 19-5-289 | FALK T10 | Direct |  |  | Yes |  | Yes | [5 empty] | 3 15/16 |  |  | 3.9370 | 3.9355 | 3.9375 | 1.0000 X 0.5000 |  |  |  | SK-19-72 | Yes | Ambient Temp F=70; Discharge Height (A)=55 13/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=3; Discharge Flange to CL (E)=36 1/2; Base Width (F)=66 1/4; Shaft Height (H)=40 1/2; Total Vert Height (TV)=88 5/8; Max Right of CL to Hsg (RH)=39 15/16; Max Left of CL to Disch (LH)=58 13/16; Base Flange to CL (D)=94 3/4; Drive End of Shaft to CL (K)=48 1/8; Mtg Flange to CL (LR)=19 9/32 | Size=4900; Design=6195; Arrangement=8S; % Width=110.0; Discharge=DB; Rotation=CCW; CFM=70630; SP=11.86; BHP=215.2; RPM=1780; Max Temp F=103; Effective Wheel Dia=46 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Hub=19-5-289; Coupling=FALK T10; Blades=10; Shaft Dia=3 15/16; Brg Centers=14; Critical Speed RPM=3360; BX=24 1/4; STB=9 7/8; OH=14.00; STH=2.94; Bearing Size=3 15/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=34 3/4; Motor Enclosure=ODP; Drive=Direct | Open
410189 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN REVISED PER FEA.txt |  |  | 410189 | 4900 | 6195 |  |  | 8S | 95.0 | TH | CW | 46 9/16 | 49441 | 20.90 | 198.7 | 1770 | 86 | 103 | 0.0716 | 300.0 | 1800 | 21936 | 3 11/16 | 14 | 3488 | 37 7/16 | 11.74 | 22 3/16 | 9 7/16 | 114 | 2.94 | 3 11/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -410 | FLOAT | 1220 | 0 | 1423 | 2000 | 1045 STEEL | 0.33 | 0.28 | 33 |  | ASTM A6 XF-100 | 1/4 | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 1/2 |  |  |  | 10 | 2120 | 3890 | [9 empty] | ODP | 2513 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 12.790 |  | Included |  | Yes | 7690 | 77529 | 19-5-289 | FALK T10 | Direct |  |  | Yes | [7 empty] | 3 11/16 |  |  | 3.6870 | 3.6855 | 3.6875 | 0.8750 X 0.4375 |  |  |  | SK-19-72 | Yes | Ambient Temp F=70; Discharge Height (A)=55 13/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=36 1/2; Base Width (F)=66 1/4; Shaft Height (H)=46 7/16; Total Vert Height (TV)=104 1/4; Max Right of CL to Hsg (RH)=36 1/2; Max Left of CL to Disch (LH)=48 1/8; Base Flange to CL (D)=92 3/4; Drive End of Shaft to CL (K)=46 1/8; Mtg Flange to CL (LR)=18 13/32 | Size=4900; Design=6195; Arrangement=8S; % Width=95.0; Discharge=TH; Rotation=CW; CFM=49441; SP=20.90; BHP=198.7; RPM=1770; Max Temp F=103; Effective Wheel Dia=46 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Hub=19-5-289; Coupling=FALK T10; Blades=10; Shaft Dia=3 11/16; Brg Centers=14; Critical Speed RPM=3488; BX=22 3/16; STB=9 7/16; OH=11.74; STH=2.94; Bearing Size=3 11/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=33; Motor Enclosure=ODP; Drive=Direct | Open
410193 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN-REVISED PER FEA.txt |  |  | 410193 | 3612 | 6195 |  |  | 8S | 110.0 | UB | CW | 34 11/16 | 26486 | 9.88 | 55.3 | 1780 | 86 | 103 | 0.0716 | 60.0 | 1800 | 17974 | 2 15/16 | 10 | 3502 | 31 3/16 | 11.55 | 19 1/8 | 8 3/8 | 60 | 2.25 | 2 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -322 | FLOAT | 727 | 0 | 409 | 2801 | 1045 STEEL | 0.20 | 0.11 | 25 7/8 |  | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 3/8 |  |  |  | 10 | 2841 | 4690 | [10 empty] | 1043 | 7 GA C.Q. HRS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 7.468 |  | Included |  | Included | 3196 | 37721 | 19-5-16 | FALK T10 | Direct |  |  | Yes |  | Yes | [5 empty] | 2 15/16 |  |  | 2.9370 | 2.9355 | 2.9375 | 0.7500 X 0.3750 |  |  |  |  | Yes | Ambient Temp F=70; Discharge Height (A)=41 9/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=27 3/4; Base Width (F)=51; Shaft Height (H)=39 7/16; Total Vert Height (TV)=67 3/16; Max Right of CL to Hsg (RH)=29 7/8; Max Left of CL to Disch (LH)=43 9/16; Base Flange to CL (D)=66 1/8; Drive End of Shaft to CL (K)=37 1/2; Mtg Flange to CL (LR)=15 15/16 | Size=3612; Design=6195; Arrangement=8S; % Width=110.0; Discharge=UB; Rotation=CW; CFM=26486; SP=9.88; BHP=55.3; RPM=1780; Max Temp F=103; Effective Wheel Dia=34 11/16; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Hub=19-5-16; Coupling=FALK T10; Blades=10; Shaft Dia=2 15/16; Brg Centers=10; Critical Speed RPM=3502; BX=19 1/8; STB=8 3/8; OH=11.55; STH=2.25; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=25 7/8; Drive=Direct | Open
410194 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN REVISED PER FEA.txt |  |  | 410194 | 4900 | 6195 |  |  | 8S | 95.0 | TAU | CW | 46 9/16 | 56504 | 17.68 | 203.6 | 1780 | 86 | 103 | 0.0716 | 300.0 | 1800 | 21936 | 3 11/16 | 14 | 3488 | 37 7/16 | 11.74 | 22 3/16 | 9 7/16 | 114 | 2.94 | 3 11/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -410 | FLOAT | 1220 | 0 | 1423 | 2000 | 1045 STEEL | 0.33 | 0.28 | 33 |  | ASTM A6 XF-100 | 1/4 | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 1/2 |  |  |  | 10 | 2120 | 3890 | [9 empty] | ODP | 3250 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 12.790 |  | Included |  | Included | 8774 | 80635 | 19-5-289 | FALK T10 | Direct |  |  | Yes | [7 empty] | 3 11/16 |  |  | 3.6870 | 3.6855 | 3.6875 | 0.8750 X 0.4375 |  |  |  | SK-19-72 | Yes | Ambient Temp F=70; Discharge Height (A)=55 13/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=36 1/2; Base Width (F)=66 1/4; Shaft Height (H)=50 1/2; Total Vert Height (TV)=117 3/16; Max Right of CL to Hsg (RH)=35 7/8; Max Left of CL to Disch (LH)=52 3/16; Base Flange to CL (D)=92 3/4; Drive End of Shaft to CL (K)=46 1/8; Mtg Flange to CL (LR)=18 13/32 | Size=4900; Design=6195; Arrangement=8S; % Width=95.0; Discharge=TAU; Rotation=CW; CFM=56504; SP=17.68; BHP=203.6; RPM=1780; Max Temp F=103; Effective Wheel Dia=46 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Hub=19-5-289; Coupling=FALK T10; Blades=10; Shaft Dia=3 11/16; Brg Centers=14; Critical Speed RPM=3488; BX=22 3/16; STB=9 7/16; OH=11.74; STH=2.94; Bearing Size=3 11/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=33; Motor Enclosure=ODP; Drive=Direct | Open
410196 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN PER FEA.txt |  |  | 410196 | 3000 | 6195 |  |  | 8S | 75.0 | UB | CW | 28 1/2 | 9005 | 7.50 | 13.3 | 1750 | 86 | 103 | 0.0716 | 15.0 | 1800 | 14773 | 2 3/16 | 11 | 3768 | 27 3/16 | 8.18 | 13 7/8 | 6 1/2 | 29 | 1.94 | 2 3/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -106 | FLOAT | 337 | 0 | 166 | 3014 | 1045 STEEL | 0.18 | 0.07 | 18 3/4 |  | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 3/8 |  |  |  | 10 | 3976 | 9620 | [10 empty] | 287 | 10 GA C.Q. HRS | SK-9-236 MED PRESSURE, 30 IN. CENTERS | 4.443 |  | Included |  | Included | 1469 | 28975 | 19-5-26 | FALK T10 | Direct |  |  | Yes |  | Yes | [5 empty] | 2 3/16 |  |  | 2.1870 | 2.1860 | 2.1875 | 0.5000 X 0.2500 |  |  |  |  | Yes | Ambient Temp F=70; Discharge Height (A)=34 1/8; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=24 3/8; Base Width (F)=44 1/4; Shaft Height (H)=32 5/8; Total Vert Height (TV)=57; Max Right of CL to Hsg (RH)=24 5/8; Max Left of CL to Disch (LH)=36 1/8; Base Flange to CL (D)=53 1/2; Drive End of Shaft to CL (K)=31 7/8; Mtg Flange to CL (LR)=11 7/8 | Size=3000; Design=6195; Arrangement=8S; % Width=75.0; Discharge=UB; Rotation=CW; CFM=9005; SP=7.50; BHP=13.3; RPM=1750; Max Temp F=103; Effective Wheel Dia=28 1/2; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Hub=19-5-26; Coupling=FALK T10; Blades=10; Shaft Dia=2 3/16; Brg Centers=11; Critical Speed RPM=3768; BX=13 7/8; STB=6 1/2; OH=8.18; STH=1.94; Bearing Size=2 3/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=18 3/4; Drive=Direct | Open
410197 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN (ONLY USE FOR STATIC AND DYNMAIC LOADS).txt |  |  | 410197 | 2700 | 6195 |  |  | 8S | 85.0 | UB | CW | 25 5/8 | 7063 | 6.83 | 9.4 | 1770 | 68 | 103 | 0.0745 | 10.0 | 1800 | 12087 | 1 7/16 | 12 | 2562 | 24 3/8 | 6.43 | 11 7/16 | 5 | 11 | 1.69 | 1 7/16 | LINK BELT SERIES 300 | 400000 | FIXED | -56 | FIXED | 200 | 40 | 89 | 2049 | 1045 STEEL | 0.42 | 0.16 | 17 1/2 |  | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 |  |  |  | 10 | 3590 | 7680 | [9 empty] | ODP | 160 | 10 GA C.Q. HRS | SK-9-236 LOW PRESSURE, 36 IN. CENTERS | 3.737 |  |  |  | Yes | 989 | 21044 | 19-5-1056 | FALK G20 | Direct |  |  |  |  | Yes | [7 empty] | Q2 BUSHING 1 7/16 | [8 empty] | Yes | Ambient Temp F=70; Discharge Height (A)=30 3/4; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=22 5/8; Base Width (F)=40 3/4; Shaft Height (H)=29 3/4; Total Vert Height (TV)=52 3/8; Max Right of CL to Hsg (RH)=22 1/4; Max Left of CL to Disch (LH)=32 3/4; Base Flange to CL (D)=47 7/16; Drive End of Shaft to CL (K)=28 7/16; Mtg Flange to CL (LR)=11 1/4 | Size=2700; Design=6195; Arrangement=8S; % Width=85.0; Discharge=UB; Rotation=CW; CFM=7063; SP=6.83; BHP=9.4; RPM=1770; Max Temp F=103; Effective Wheel Dia=25 5/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=19-5-1056; Coupling=FALK G20; Blades=10; Shaft Dia=1 7/16; Brg Centers=12; Critical Speed RPM=2562; BX=11 7/16; STB=5; OH=6.43; STH=1.69; Bearing Size=1 7/16; Bearing Series=LINK BELT SERIES 300; Housing Width (N)=17 1/2; Motor Enclosure=ODP; Drive=Direct | Open
410198 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN REVISED PER FEA.txt |  |  | 410198 | 5414 | 6195 |  |  | 8S | 75.0 | TAU | CCW | 51 9/16 | 63214 | 20.70 | 272.1 | 1780 | 86 | 86 | 0.0720 | 300.0 | 1800 | 24287 | 4 3/16 | 14 | 3545 | 39 3/4 | 12.99 | 23 13/16 | 10 1/8 |  | 3.38 | 4 3/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -633 | FLOAT | 1689 | 0 | 2148 | 1900 | 1045 STEEL | 0.25 | 0.19 | 33 7/8 |  | ASTM A6 XF-100 | 5/16 | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 1/2 |  |  |  | 10 | 2233 | 4230 | [9 empty] | ODP | 3250 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 14.526 |  | Included |  | Yes | 9763 | 96346 | 19-5-12 | FALK T10 | Direct |  |  | Yes | [7 empty] | 4 3/16 |  |  | 4.1870 | 4.1855 | 4.1875 | 1.0000 X 0.5000 |  |  |  | SK-19-72 | Yes | Ambient Temp F=70; Discharge Height (A)=61 3/4; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=40 3/8; Base Width (F)=72 1/2; Shaft Height (H)=57 3/16; Total Vert Height (TV)=130 13/16; Max Right of CL to Hsg (RH)=57 11/16; Max Left of CL to Disch (LH)=39 5/8; Base Flange to CL (D)=94 7/8; Drive End of Shaft to CL (K)=47 15/16; Mtg Flange to CL (LR)=19 3/16 | Size=5414; Design=6195; Arrangement=8S; % Width=75.0; Discharge=TAU; Rotation=CCW; CFM=63214; SP=20.70; BHP=272.1; RPM=1780; Max Temp F=86; Effective Wheel Dia=51 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=5/16; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Hub=19-5-12; Coupling=FALK T10; Blades=10; Shaft Dia=4 3/16; Brg Centers=14; Critical Speed RPM=3545; BX=23 13/16; STB=10 1/8; OH=12.99; STH=3.38; Bearing Size=4 3/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=33 7/8; Motor Enclosure=ODP; Drive=Direct | Open
410199 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN REVISED PER FEA.txt |  |  | 410199 | 4900 | 6195 |  |  | 8S | 95.0 | TAU | CCW | 46 9/16 | 56504 | 17.68 | 203.6 | 1780 | 86 | 103 | 0.0716 | 300.0 | 1800 | 21936 | 3 11/16 | 14 | 3488 | 37 7/16 | 11.74 | 22 3/16 | 9 7/16 | 114 | 2.94 | 3 11/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -410 | FLOAT | 1220 | 0 | 1423 | 2000 | 1045 STEEL | 0.33 | 0.28 | 33 |  | ASTM A6 XF-100 | 1/4 | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 1/2 |  |  |  | 10 | 2120 | 3890 | [9 empty] | ODP | 3250 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 12.790 |  | Included |  | Included | 8774 | 80635 | 19-5-289 | FALK T10 | Direct |  |  | Yes | [7 empty] | 3 11/16 |  |  | 3.6870 | 3.6855 | 3.6875 | 0.8750 X 0.4375 |  |  |  | SK-19-72 | Yes | Ambient Temp F=70; Discharge Height (A)=55 13/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=36 1/2; Base Width (F)=66 1/4; Shaft Height (H)=50 1/2; Total Vert Height (TV)=117 3/16; Max Right of CL to Hsg (RH)=52 3/16; Max Left of CL to Disch (LH)=35 7/8; Base Flange to CL (D)=92 3/4; Drive End of Shaft to CL (K)=46 1/8; Mtg Flange to CL (LR)=18 13/32 | Size=4900; Design=6195; Arrangement=8S; % Width=95.0; Discharge=TAU; Rotation=CCW; CFM=56504; SP=17.68; BHP=203.6; RPM=1780; Max Temp F=103; Effective Wheel Dia=46 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Hub=19-5-289; Coupling=FALK T10; Blades=10; Shaft Dia=3 11/16; Brg Centers=14; Critical Speed RPM=3488; BX=22 3/16; STB=9 7/16; OH=11.74; STH=2.94; Bearing Size=3 11/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=33; Motor Enclosure=ODP; Drive=Direct | Open
410201 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN REVISED PER FEA.txt |  |  | 410201 | 4900 | 6195 |  |  | 8S | 95.0 | TH | CCW | 46 9/16 | 49441 | 20.90 | 198.7 | 1770 | 86 | 103 | 0.0716 | 300.0 | 1800 | 21936 | 3 11/16 | 14 | 3488 | 37 7/16 | 11.74 | 22 3/16 | 9 7/16 | 114 | 2.94 | 3 11/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -410 | FLOAT | 1220 | 0 | 1423 | 2000 | 1045 STEEL | 0.33 | 0.28 | 33 |  | ASTM A6 XF-100 | 1/4 | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 1/2 |  |  |  | 10 | 2120 | 3890 | [9 empty] | ODP | 2513 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 12.790 |  | Included |  | Yes | 7690 | 77529 | 19-5-289 | FALK T10 | Direct |  |  | Yes | [7 empty] | 3 11/16 |  |  | 3.6870 | 3.6855 | 3.6875 | 0.8750 X 0.4375 |  |  |  | SK-19-72 | Yes | Ambient Temp F=70; Discharge Height (A)=55 13/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=36 1/2; Base Width (F)=66 1/4; Shaft Height (H)=46 7/16; Total Vert Height (TV)=104 1/4; Max Right of CL to Hsg (RH)=48 1/8; Max Left of CL to Disch (LH)=36 1/2; Base Flange to CL (D)=92 3/4; Drive End of Shaft to CL (K)=46 1/8; Mtg Flange to CL (LR)=18 13/32 | Size=4900; Design=6195; Arrangement=8S; % Width=95.0; Discharge=TH; Rotation=CCW; CFM=49441; SP=20.90; BHP=198.7; RPM=1770; Max Temp F=103; Effective Wheel Dia=46 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Hub=19-5-289; Coupling=FALK T10; Blades=10; Shaft Dia=3 11/16; Brg Centers=14; Critical Speed RPM=3488; BX=22 3/16; STB=9 7/16; OH=11.74; STH=2.94; Bearing Size=3 11/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=33; Motor Enclosure=ODP; Drive=Direct | Open
410317 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.txt |  |  | 410317 | 3612 | 1904 |  | PACKAGED FORCED DRAFT FAN | 4S1 | 70.0 | DB | CW | 40 1/8 | 17206 | 13.31 | 50.0 | 1746 | 200 | 200 | 0.0530 | 50.0 | 1800 | 18920 | [8 empty] | 2.25 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 1/4 |  |  |  | 10 | 2111 | 2640 | 205 | 197 | 289 | 3.86 | 4.50 |  |  | 326T |  | TEFC | 762 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 6.458 |  | Not included |  |  |  |  | 19-5-1057 |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q1 BUSHING 2 1/8 |  |  |  |  | 65 3/4 | 13 15/16 | 7 |  |  | Ambient Temp F=90 | Size=3612; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S1; % Width=70.0; Discharge=DB; Rotation=CW; CFM=17206; SP=13.31; BHP=50.0; RPM=1746; Max Temp F=200; Effective Wheel Dia=40 1/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Hub=19-5-1057; Blades=10; STH=2.25; Motor Frame=326T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
410389 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 410389 | 16 | A10 |  |  | 4S | 90.0 | BAU | CW |  | 1000 | 1.00 | 10.0 | 3500 | 140 | 140 | 0.0750 | 10.0 | 3500 | 16313 | [8 empty] | 1.68 | [15 empty] | ALUM 5052-H32 | 0.125 | ALUM 3003-O | 0.125 | ALUM 5052-H32 | 0.125 |  |  |  | 8 | 4763 | 12790 | 13 | 31 | 4 | 3.27 | 3.87 |  |  | 213T |  | ODP | 145 | 10 GA C.Q. HRS | SK-9-236 MED PRESSURE, 30 IN. CENTERS | 1.568 |  | Not included |  |  |  |  | 4-5-33 |  | Motor mounted |  |  |  |  | Yes | [17 empty] | Ambient Temp F=90 | Size=16; Design=A10; Arrangement=4S; % Width=90.0; Discharge=BAU; Rotation=CW; CFM=1000; SP=1.00; BHP=10.0; RPM=3500; Max Temp F=140; Blade Material=ALUM 5052-H32; Blade Gauge=0.125; Sideplate Material=ALUM 3003-O; Sideplate Gauge=0.125; Backplate Material=ALUM 5052-H32; Backplate Gauge=0.125; Hub=4-5-33; Blades=8; STH=1.68; Motor Frame=213T; Motor Enclosure=ODP; Drive=Motor mounted | Open
410511 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.txt |  |  | 410511 | 3000 | 1902 |  | PACKAGED FORCED DRAFT FAN | 4S1 | 100.0 | DB | CW |  | 25099 | 28.10 | 141.5 | 3550 | 101 | 101 | 0.0674 | 150.0 | 3600 | 28274 | [8 empty] | 1.94 | [15 empty] | ASTM A1011-HSLAS | 0.105 (12) | ASTM A572 X-TEN | 5/16 | ASTM A1011-HSLAS | 0.135 (10) |  |  |  | 10 | 3648 | 4960 | 200 | 273 | 145 | 5.23 | 6.69 |  |  | 445T |  | TEFC | 2231 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 4.858 | 33.000 | Not included |  |  | 4659 | 52678 | 19-5-11 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 3 3/8 | [6 empty] | 59 1/2 | 12 5/8 | 1 |  |  | Ambient Temp F=90 | Size=3000; Design=1902; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S1; % Width=100.0; Discharge=DB; Rotation=CW; CFM=25099; SP=28.10; BHP=141.5; RPM=3550; Max Temp F=101; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=5/16; Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.135 (10); Hub=19-5-11; Blades=10; STH=1.94; Motor Frame=445T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
410559 | GENERAL LINE | NO FIELDS | pdf | 370-23-1469 D64 Wheel Construction (Inner Ring).pdf | [105 empty] | Open
410575 | GENERAL LINE | OK | pdf_vision | 410575 QT RUN.pdf |  |  | 410575 | 3000 | 2300B |  |  | 8S | 100.0 | TH | CW | 30 | 5539 | 36.62 | 54.6 | 3550 | 280 | 300 | 0.0526 | 75.0 | 3600 |  | 2 15/16 | 13 1/2 | 8015 | 31 5/16 | 7.12 | 8 1/4 | 7 3/4 | 60 | 0.00 | 2 15/16 | LINK BELT SERIES 300 | 131790 | FIXED | -22 | FLOAT | 249 | 0 |  |  |  | 0.10 | 0.08 | [21 empty] | 365TS |  |  | 920 |  | SK-9-236 HI PRESSURE, 18 IN. CENTERS | [8 empty] | FALK T10, SIZE 1030T, BORE 2.938 NOT INCL. | Direct |  |  |  |  | Yes | [5 empty] | 2 15/16 | [10 empty] | Yes | Ambient Temp F=90; Coupling Ref=SKE-9-356; Clearance Fit=4-5-202-2 | Size=3000; Design=2300B; Arrangement=8S; % Width=100.0; Discharge=TH; Rotation=CW; CFM=5539; SP=36.62; BHP=54.6; RPM=3550; Max Temp F=300; Effective Wheel Dia=30; Coupling=FALK T10, SIZE 1030T, BORE 2.938 NOT INCL.; Shaft Dia=2 15/16; Brg Centers=13 1/2; Critical Speed RPM=8015; BX=8 1/4; STB=7 3/4; OH=7.12; STH=0.00; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=365TS; Drive=Direct | Open
410582 | GENERAL LINE | OK | cbc_qt_run_text | QT Run.txt |  |  | 410582 | 3612 | 6195 |  |  | 9H | 100.0 | TAU | CW | 34 11/16 | 26956 | 15.84 | 85.6 | 2151 | 100 | 425 | 0.0749 | 100.0 | 2151 | 19527 | 3 3/16 | 12 | 3502 | 38 9/16 | 12.80 | 19 15/16 | 12 1/2 | 87 | 2.25 | 3 3/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 1650 | FIXED | 544 | 190 | 365 | 2600 | 1045 STEEL | 0.21 | 0.45 | 25 | 25 1/2 | ASTM A6 XF-100 | 1/4 | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 5/16 |  |  |  | 10 | 3095 | 4510 | [5 empty] | 7.1 | 3.2 | 404 | Z | ODP | 1145 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 7.216 |  | Included |  | Included | 3619 | 55365 | 19-5-16 |  | Belt |  |  | Yes |  | Yes | [5 empty] | 3 3/16 | [10 empty] | Yes | Ambient Temp F=70; Discharge Height (A)=41 9/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=27 3/4; Unitary Base To Cl (LB)=71 7/16; Motor Cl To Fan Cl (LM)=50 13/16; Shaft Height (H)=41 7/16; Total Vert Height (TV)=91 7/8; Max Right of CL to Hsg (RH)=26 13/16; Max Left of CL to Disch (LH)=39; Mounting Channel (MA)=2 1/4; Base Flange to CL (D)=36 7/16; Drive End of Shaft to CL (K)=44 7/16; Mtg Flange to CL (LR)=14 3/4 | Size=3612; Design=6195; Arrangement=9H; % Width=100.0; Discharge=TAU; Rotation=CW; CFM=26956; SP=15.84; BHP=85.6; RPM=2151; Max Temp F=425; Effective Wheel Dia=34 11/16; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=19-5-16; Blades=10; Shaft Dia=3 3/16; Brg Centers=12; Critical Speed RPM=3502; BX=19 15/16; STB=12 1/2; OH=12.80; STH=2.25; Bearing Size=3 3/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=25; Base to CL (F)=25 1/2; Motor Frame=404; Motor Position=Z; Motor Enclosure=ODP; Drive=Belt | Open
410614 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN 9-5-23.txt |  |  | 410614 | 4014 | 1904 |  | PACKAGED FORCED DRAFT FAN | 4S | 70.0 | DB | CW | 44 1/4 | 22141 | 21.80 | 97.8 | 1770 | 105 | 105 | 0.0688 | 125.0 | 1800 | 20864 | [8 empty] | 2.50 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 5/16 |  |  |  | 10 | 2207 | 2760 | 295 | 292 | 476 | 4.15 | 6.38 |  |  | 444T |  | TEFC | 1893 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 7.914 |  | Not included |  | Yes |  |  | 19-5-16 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 3 3/8 | [9 empty] | SK-19-72 |  | Ambient Temp F=90 | Size=4014; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S; % Width=70.0; Discharge=DB; Rotation=CW; CFM=22141; SP=21.80; BHP=97.8; RPM=1770; Max Temp F=105; Effective Wheel Dia=44 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=5/16; Hub=19-5-16; Blades=10; STH=2.50; Motor Frame=444T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
410615 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN 9-5-23.txt |  |  | 410614 | 4014 | 1904 |  | PACKAGED FORCED DRAFT FAN | 4S | 70.0 | DB | CW | 44 1/4 | 22141 | 21.80 | 97.8 | 1770 | 105 | 105 | 0.0688 | 125.0 | 1800 | 20864 | [8 empty] | 2.50 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 5/16 |  |  |  | 10 | 2207 | 2760 | 295 | 292 | 476 | 4.15 | 6.38 |  |  | 444T |  | TEFC | 1893 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 7.914 |  | Not included |  | Yes |  |  | 19-5-16 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 3 3/8 | [9 empty] | SK-19-72 |  | Ambient Temp F=90 | Size=4014; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S; % Width=70.0; Discharge=DB; Rotation=CW; CFM=22141; SP=21.80; BHP=97.8; RPM=1770; Max Temp F=105; Effective Wheel Dia=44 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=5/16; Hub=19-5-16; Blades=10; STH=2.50; Motor Frame=444T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
410694 | GENERAL LINE | OK | pdf_vision | 410694 QT RUN.pdf |  |  | 410694 | 39 | STD | SIR |  | 8S | 90.0 | DISCH BAU, ROT CW | CW | 542 | 60000 | 11.00 | 139.7 | 1170 | 70 | 70 | 0.0727 | 150.0 | 1200 | 16610 | 3 7/16 | 31 1/8 | 2150 | 58 9/16 | 14.59 | 27 1/16 | 8 3/4 | 154 | 1119 | 3 7/16 | 7/16 FAB. STL. | 400000 | FIXED | -109 | FIXED | 714 | 296 | 1080 |  |  | 0.31 | 0.25 |  |  | ASTM A572 X-TEN | 1/4 | ASTM A1011-HSLAS | 0.105 (12) | ASTM A572 X-TEN | 5/16 |  |  |  | 8 | 1354 | 2050 | [7 empty] | 447T |  |  |  |  | SK-9-236 MED PRESSURE, 24 IN. CENTERS | [7 empty] | 4-5-122 | FALK T10, SIZE 1090T, BORE 3.438 | Direct |  |  |  |  | Yes | [16 empty] | Yes | Ambient Temp F=90 | Size=39; Design=STD; Arrangement=8S; % Width=90.0; Discharge=DISCH BAU, ROT CW; Rotation=CW; Class=SIR; CFM=60000; SP=11.00; BHP=139.7; RPM=1170; Max Temp F=70; Effective Wheel Dia=542; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=4-5-122; Coupling=FALK T10, SIZE 1090T, BORE 3.438; Blades=8; Shaft Dia=3 7/16; Brg Centers=31 1/8; Critical Speed RPM=2150; BX=27 1/16; STB=8 3/4; OH=14.59; STH=1119; Bearing Size=3 7/16; Bearing Series=7/16 FAB. STL.; Motor Frame=447T; Drive=Direct | Open
410770 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN (ONLY USE FOR STATIC & DYNAMIC LOADS!).txt |  |  | 410770 | 4900 | 6100 |  |  | 8S | 65.0 | UB | CW |  | 47850 | 12.00 | 150.0 | 1770 | 70 | 70 | 0.0648 | 150.0 | 1800 | 23091 | 2 11/16 | 16 | 2533 | 35 13/16 | 9.71 | 18 7/8 | 7 7/8 |  | 2.94 | 2 11/16 | LINK BELT SERIES 6800 | 127959 | FIXED | -220 | FLOAT | 834 | 0 | 1123 | 1936 | 1045 STEEL | 0.60 | 0.35 |  |  | ASTM A572 X-TEN | 5/16 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  |  | 10 | 1936 | 4020 | [7 empty] | 445T |  |  | 1785 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 11.434 |  |  |  | Yes | 6384 | 58249 | 19-5-289 | FALK G20 | Direct |  |  |  | Yes | Yes | [5 empty] | 2 7/16 | [9 empty] | SK-19-72 | Yes | Ambient Temp F=70 | Size=4900; Design=6100; Arrangement=8S; % Width=65.0; Discharge=UB; Rotation=CW; CFM=47850; SP=12.00; BHP=150.0; RPM=1770; Max Temp F=70; Blade Material=ASTM A572 X-TEN; Blade Gauge=5/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=19-5-289; Coupling=FALK G20; Blades=10; Shaft Dia=2 11/16; Brg Centers=16; Critical Speed RPM=2533; BX=18 7/8; STB=7 7/8; OH=9.71; STH=2.94; Bearing Size=2 11/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=445T; Drive=Direct | Open
410771 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN (ONLY USE FOR STATIC & DYNAMIC LOADS!).txt |  |  | 410770 | 4900 | 6100 |  |  | 8S | 65.0 | UB | CCW |  | 47850 | 12.00 | 150.0 | 1770 | 70 | 70 | 0.0648 | 150.0 | 1800 | 23091 | 2 11/16 | 16 | 2533 | 35 13/16 | 9.71 | 18 7/8 | 7 7/8 |  | 2.94 | 2 11/16 | LINK BELT SERIES 6800 | 127959 | FIXED | -220 | FLOAT | 834 | 0 | 1123 | 1936 | 1045 STEEL | 0.60 | 0.35 |  |  | ASTM A572 X-TEN | 5/16 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  |  | 10 | 1936 | 4020 | [7 empty] | 445T |  |  | 1785 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 11.434 |  |  |  | Yes | 6384 | 58249 | 19-5-289 | FALK G20 | Direct |  |  |  | Yes | Yes | [5 empty] | 2 7/16 | [9 empty] | SK-19-72 | Yes | Ambient Temp F=70 | Size=4900; Design=6100; Arrangement=8S; % Width=65.0; Discharge=UB; Rotation=CCW; CFM=47850; SP=12.00; BHP=150.0; RPM=1770; Max Temp F=70; Blade Material=ASTM A572 X-TEN; Blade Gauge=5/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=19-5-289; Coupling=FALK G20; Blades=10; Shaft Dia=2 11/16; Brg Centers=16; Critical Speed RPM=2533; BX=18 7/8; STB=7 7/8; OH=9.71; STH=2.94; Bearing Size=2 11/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=445T; Drive=Direct | Open
410827 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN 9-15-23.txt |  |  | 410827 | 4014 | 1904 |  | PACKAGED FORCED DRAFT FAN | 4S1 | 70.0 | DB | CCW | 44 1/4 | 23561 | 20.93 | 99.2 | 1770 | 100 | 100 | 0.0695 | 125.0 | 1785 | 20690 | [8 empty] | 2.50 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 5/16 |  |  |  | 10 | 2207 | 2760 | 295 | 287 | 476 | 4.15 | 6.38 |  |  | 444T |  | TEFC | 1893 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 7.914 |  | Not included |  |  |  |  | 19-5-16 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 3 3/8 | [6 empty] | 73 | 15 9/16 | 1 |  |  | Ambient Temp F=90 | Size=4014; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S1; % Width=70.0; Discharge=DB; Rotation=CCW; CFM=23561; SP=20.93; BHP=99.2; RPM=1770; Max Temp F=100; Effective Wheel Dia=44 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=5/16; Hub=19-5-16; Blades=10; STH=2.50; Motor Frame=444T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
410887 | HDX | OK | pdf_vision | QT RUN-CO#2.pdf |  |  | SN#410887-CO#2 | 5414 | 6105 | ARR 8S |  | 8S | 100.0 | DISCH BH | RCT CCW | 56 15/16 | 149 | 37.10 | 474.4 | 1780 | 165 | 165 | 0.0633 | 500.0 | 1800 | 26843 | 5 3/16 | 16 | 3071 | 47 1/2 | 18.70 | 29 11/16 | 11 | 5/8 | MI.5 | 5 3/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -968 | FLOAT | 2256 | 0 | 2610 | 1801 | [5 empty] | ASTM A6 | 3/8 | ASTM A6 | 5/16 | ASTM A572 | 1/2 |  |  | BORE 4 15/16 CAST STEEL | 10 | 1801 | 2900 | [7 empty] | 449T |  | TEFC | 3250 | 5/16 C.Q. HRS | SK-9-236 HI PRESSURE, 19 IN. CENTERS |  |  |  |  | Included | 12184 | 131413 | WHEEL HUB NOMINAL BORE = 4.9375 | FALK T10, SIZE 1100T, BORE 3.438 | Direct |  | Required | Yes | Yes | [6 empty] | 4 15/16 |  |  | 3.4370 | 3.4355 | 3.4375 | 0.8750 X 0.4375 |  |  |  |  | Yes | Ambient Temp F=70 F | Size=5414; Design=6105; Arrangement=8S; % Width=100.0; Discharge=DISCH BH; Rotation=RCT CCW; Class=ARR 8S; CFM=149; SP=37.10; BHP=474.4; RPM=1780; Max Temp F=165; Effective Wheel Dia=56 15/16; Blade Material=ASTM A6; Blade Gauge=3/8; Sideplate Material=ASTM A6; Sideplate Gauge=5/16; Backplate Material=ASTM A572; Backplate Gauge=1/2; Wheel Material=BORE 4 15/16 CAST STEEL; Hub=WHEEL HUB NOMINAL BORE = 4.9375; Coupling=FALK T10, SIZE 1100T, BORE 3.438; Blades=10; Shaft Dia=5 3/16; Brg Centers=16; Critical Speed RPM=3071; BX=29 11/16; STB=11; OH=18.70; STH=MI.5; Bearing Size=5 3/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=449T; Motor Enclosure=TEFC; Drive=Direct | Open
410887 | HDX | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | SN#410887 | 5 | 6105 | 100.0 PCT |  | 98 | 100.0 | BH | CW | 56 15/16 | 68149 | 37.10 | 474.4 | 1780 | 70 | 165 | 0.0633 | 500.0 | 1800 | 26843 | 5 3/16 | 16 | 3071 | 47 1/2 | 18.70 | 29 11/16 | 11 5/8 |  | 3.38 | 5 3/16 | 6800 | 400000 | FIXED | -968 | FLOAT | 2256 | 0 | 2610 | 1801 |  | 0.24 | 0.18 |  |  | ASTM A6 XF-100 | 3/8 | ASTM A6 XF-100 | 5/16 | ASTM A572 X-TEN | 1/2 |  |  | CAST STEEL | 10 | 1801 | 2900 | [9 empty] | TEFC | 3250 | 5/16 C.Q. HRS | SK-9-236 HI PRESSURE, 19 IN. CENTERS | 15.920 |  |  |  | Included | 12184 | 131413 | BORE 4 17/16 | FAIK T10 | Direct |  |  |  | Yes | [6 empty] | 4 17/16 |  |  | 3.4370 | 3.4355 | 3.4375 | 0.8750 X 0.4375 |  |  |  | SK-19-72 | Yes | Ambient Temp F=70 | Size=5; Design=6105; Arrangement=98; % Width=100.0; Discharge=BH; Rotation=CW; Class=100.0 PCT; CFM=68149; SP=37.10; BHP=474.4; RPM=1780; Max Temp F=165; Effective Wheel Dia=56 15/16; Blade Material=ASTM A6 XF-100; Blade Gauge=3/8; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=5/16; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Wheel Material=CAST STEEL; Hub=BORE 4 17/16; Coupling=FAIK T10; Blades=10; Shaft Dia=5 3/16; Brg Centers=16; Critical Speed RPM=3071; BX=29 11/16; STB=11 5/8; OH=18.70; STH=3.38; Bearing Size=5 3/16; Bearing Series=6800; Motor Enclosure=TEFC; Drive=Direct | Open
411028 | HDX | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | 411028 | 6000 | 1904 |  |  | 381 | 110.0 | UB | CCW | 66 | 120780 | 34.63 | 775.1 | 1780 | 235 | 260 | 0.0461 | 800.0 | 1800 | 31102 | 7 | 91 3/8 | 2341 | 105.31 | 19.65 | 79.25 | 9.75 | 932 | 4.12 | 3/16 | 6800 | 400000 | FLOAT | 2001 | FIXED | 844 | 1441 | 7088 | 1872 |  | 0.17 | 0.56 |  |  | ASTM A6 XF-100 | 3/16 | ASTM A6 XF-100 | 3/8 | ASTM A572 X-TEN | 3/4 |  |  | CAST STEEL | 10 | 1939 | 2420 | [11 empty] | 3/8 C.Q. HRS | SK-9-236 HI PRESSURE, 18 IN. CENTERS | 20.262 | 73.000 |  |  |  | 13767 | 188102 | 19-5-218 | FALK G20, SIZE 1035G | NON-NEMA MOTOR |  | Required |  | Yes | [9 empty] | 4.1870 | 4.1855 |  | 1.0000 X 0.5000 | 131 1/2 | 27 7/8 | 270 | SK-19-72 | Yes | Ambient Temp F=90 | Size=6000; Design=1904; Arrangement=381; % Width=110.0; Discharge=UB; Rotation=CCW; CFM=120780; SP=34.63; BHP=775.1; RPM=1780; Max Temp F=260; Effective Wheel Dia=66; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=3/8; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/4; Wheel Material=CAST STEEL; Hub=19-5-218; Coupling=FALK G20, SIZE 1035G; Blades=10; Shaft Dia=7; Brg Centers=91 3/8; Critical Speed RPM=2341; BX=79.25; STB=9.75; OH=19.65; STH=4.12; Bearing Size=3/16; Bearing Series=6800; Drive=NON-NEMA MOTOR | Open
411091 | HDX | CHECK VISION | pdf_vision | QT RUN-REV.A.pdf |  |  | SN411091, FD FAN | 1900 | 4900 | 5500 |  | ARR 781,100.0 PCT | 100.0 | DISCH TH | ROT CW | 49 1/2 | 32325 | 25.50 | 161.2 | 1775 | 100 | 150 | 0.0580 | 200.0 | 1800 | 23326 | 2 11/16 | 46 13/16 | 2911 |  |  |  | 8.75 |  | 2.00 | 2 7/16 | 6800 | 400000 | FLOAT | 348 | FIXED | 85 | 344 | 540 | 2079 | 1045 STEEL | 0.52 | 0.68 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 (7) |  |  | CAST STEEL | 16 | 2382 | [8 empty] | 447T |  |  |  | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 6.293 | [6 empty] | 49-5-145- | FALK T10, SIZE 1100T, BORE 2 7/16 | DRIVE-FLOAT |  |  |  | Yes | Yes | [5 empty] | 2 11/16 |  |  | 2.4370 | 2.4360 |  | 0.6250 X 0.3125 | 66 3/4 | 21 1/16 | 1 |  | Yes | Ambient Temp F=10 | Size=1900; Design=4900; Arrangement=ARR 781,100.0 PCT; % Width=100.0; Discharge=DISCH TH; Rotation=ROT CW; Class=5500; CFM=32325; SP=25.50; BHP=161.2; RPM=1775; Max Temp F=150; Effective Wheel Dia=49 1/2; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 (7); Wheel Material=CAST STEEL; Hub=49-5-145-; Coupling=FALK T10, SIZE 1100T, BORE 2 7/16; Blades=16; Shaft Dia=2 11/16; Brg Centers=46 13/16; Critical Speed RPM=2911; STB=8.75; STH=2.00; Bearing Size=2 7/16; Bearing Series=6800; Motor Frame=447T; Drive=DRIVE-FLOAT | Open
411165 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.txt |  |  | 411165 | 4014 | 1903 |  | PACKAGED FORCED DRAFT FAN | 4S | 55.0 | DB | CW | 42 1/4 | 16851 | 17.94 | 61.0 | 1770 | 100 | 100 | 0.0695 | 75.0 | 1800 | 19916 | [8 empty] | 2.50 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 1/4 |  |  |  | 10 | 2256 | 2820 | 209 | 255 | 312 | 3.82 | 4.75 |  |  | 365T |  | TEFC | 1150 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 7.437 |  | Not included |  | Yes |  |  | 19-5-1057 |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q1 BUSHING 2 3/8 | [7 empty] | SK-19-72 |  | Ambient Temp F=90 | Size=4014; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S; % Width=55.0; Discharge=DB; Rotation=CW; CFM=16851; SP=17.94; BHP=61.0; RPM=1770; Max Temp F=100; Effective Wheel Dia=42 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Hub=19-5-1057; Blades=10; STH=2.50; Motor Frame=365T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
411165 | HD-PFD-IAF | NO FIELDS | qt_run_text | QT RUN INPUTS.docx | [105 empty] | Open
411180 | HD-PFD-IAF | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | SN#411180 | 5414 | 5500 | ARR 8S |  | 8S | 100.0 | BH | CW | 53 3/4 | 3514 | 20.00 | 145.8 | 1800 | 518 | 518 | 0.0390 | 200.0 | 1800 | 25329 | 3 7/16 | 16 | 3506 | 40 5/16 | 11.25 | 18 3/4 | 9 7/8 |  | 2.19 | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -211 | FLOAT | 828 | 0 | 1039 | 1947 | 1045 STEEL | 0.46 | 0.26 |  |  | ASTM A1011-HSLAS | 0.179 (7) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A572 X-TEN | 5/16 |  |  | CAST STEEL | 16 | 1965 | [8 empty] | 447T |  | ODP | 2280 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 7.701 |  |  |  | Included | 8052 | 90139 | 23-5-424 | FALK T10, SIZE 1100T | Direct |  | Required |  | Yes | Yes | [8 empty] | 3.4370 | 3.4355 | 3.4375 | 0.8750 X 0.4375 |  |  |  | SK-55-11 | Yes | Ambient Temp F=90 | Size=5414; Design=5500; Arrangement=8S; % Width=100.0; Discharge=BH; Rotation=CW; Class=ARR 8S; CFM=3514; SP=20.00; BHP=145.8; RPM=1800; Max Temp F=518; Effective Wheel Dia=53 3/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 (7); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Wheel Material=CAST STEEL; Hub=23-5-424; Coupling=FALK T10, SIZE 1100T; Blades=16; Shaft Dia=3 7/16; Brg Centers=16; Critical Speed RPM=3506; BX=18 3/4; STB=9 7/8; OH=11.25; STH=2.19; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=447T; Motor Enclosure=ODP; Drive=Direct | Open
411189 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 411189 | 4412 | 6195 |  |  | 9H1 | 100.0 | TAU | CCW | 42 1/4 | 38000 | 14.00 | 106.9 | 1686 | 120 | 120 | 0.0685 | 125.0 | 1686 | 18660 | 3 11/16 | 14 | 3261 | 41 9/16 | 14.05 | 23 1/16 | 12 1/8 | 126 | 2.81 | 3 11/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 1922 | FIXED | 713 | 258 | 822 | 1791 | 1045 STEEL | 0.20 | 0.35 | 30 5/8 | 30 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  |  | 10 | 1791 | 3160 | [5 empty] | 9.1 | 3.7 | 444T | W |  | 1515 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 10.767 |  | Included |  |  | 7628 | 86658 | 19-5-219 |  | Belt |  |  | Yes |  | Yes | [5 empty] | 3 11/16 | [6 empty] | 80 | 17 | 1 |  | Yes | Ambient Temp F=70; Discharge Height (A)=50 5/8; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=59 5/8; Unitary Base to CL (RB)=81 1/2; Motor CL to Fan CL (RM)=59 5/8; Inlet Box Width (B)=80; Inlet Box Length To Cl (J)=44 1/4; Shaft Height (H)=48 1/2; Total Vert Height (TV)=127 7/8; Max Right of CL to Hsg (RH)=47 3/8; Max Left of CL to Disch (LH)=43 9/16; Mounting Channel (MA)=2 1/4; Base Flange to CL (D)=42 15/16; Drive End of Shaft to CL (K)=49 3/16; Box Cl To Hsg Cl (P)=34 13/16; Box Width Os (C)=17; Mtg Flange to CL (LR)=46 5/16 | Size=4412; Design=6195; Arrangement=9H1; % Width=100.0; Discharge=TAU; Rotation=CCW; CFM=38000; SP=14.00; BHP=106.9; RPM=1686; Max Temp F=120; Effective Wheel Dia=42 1/4; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=19-5-219; Blades=10; Shaft Dia=3 11/16; Brg Centers=14; Critical Speed RPM=3261; BX=23 1/16; STB=12 1/8; OH=14.05; STH=2.81; Bearing Size=3 11/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=30 5/8; Base to CL (F)=30 1/4; Motor Frame=444T; Motor Position=W; Drive=Belt | Open
411190 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 411190 | 4412 | 6195 |  |  | 9H1 | 100.0 | TAU | CW | 42 1/4 | 38000 | 14.00 | 106.9 | 1686 | 120 | 120 | 0.0685 | 125.0 | 1686 | 18660 | 3 11/16 | 14 | 3261 | 41 9/16 | 14.05 | 23 1/16 | 12 1/8 | 126 | 2.81 | 3 11/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 1922 | FIXED | 713 | 258 | 822 | 1791 | 1045 STEEL | 0.20 | 0.35 | 30 5/8 | 30 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  |  | 10 | 1791 | 3160 | [5 empty] | 9.1 | 3.7 | 444T | W |  | 1515 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 10.767 |  | Included |  |  | 7628 | 86658 | 19-5-219 |  | Belt |  |  | Yes |  | Yes | [5 empty] | 3 11/16 | [6 empty] | 80 | 17 | 1 |  | Yes | Ambient Temp F=70; Discharge Height (A)=50 5/8; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=59 5/8; Unitary Base to CL (RB)=81 1/2; Motor CL to Fan CL (RM)=59 5/8; Inlet Box Width (B)=80; Inlet Box Length To Cl (J)=44 1/4; Shaft Height (H)=48 1/2; Total Vert Height (TV)=127 7/8; Max Right of CL to Hsg (RH)=43 9/16; Max Left of CL to Disch (LH)=47 3/8; Mounting Channel (MA)=2 1/4; Base Flange to CL (D)=42 15/16; Drive End of Shaft to CL (K)=49 3/16; Box Cl To Hsg Cl (P)=34 13/16; Box Width Os (C)=17; Mtg Flange to CL (LR)=46 5/16 | Size=4412; Design=6195; Arrangement=9H1; % Width=100.0; Discharge=TAU; Rotation=CW; CFM=38000; SP=14.00; BHP=106.9; RPM=1686; Max Temp F=120; Effective Wheel Dia=42 1/4; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=19-5-219; Blades=10; Shaft Dia=3 11/16; Brg Centers=14; Critical Speed RPM=3261; BX=23 1/16; STB=12 1/8; OH=14.05; STH=2.81; Bearing Size=3 11/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=30 5/8; Base to CL (F)=30 1/4; Motor Frame=444T; Motor Position=W; Drive=Belt | Open
411306 | HDX | CHECK VISION | pdf_vision | QT RUN-CO#1.pdf |  |  | SN411306 3154 | 6600 | 1910 |  |  | 781,100.0 PCT | 100.0 | TH | ROT CCW |  | 123323 | 11.26 | 286.0 | 1185 | 425 | 500 | 0.0419 | 300.0 | 1303 | 24293 | 6 3/4 | 105 13/16 | 1899 | 119.00 | 20.02 | 93.75 | 9.62 | 39.00 | 4.94 | 3 7/16 | 6800 | 400000 | FIXED | 1899 | FLOAT | 795 | 0 |  | 1356 | 1045 STEEL | 0.17 | 0.58 |  |  | ASTM A1011-HSLAS | 0.105 (12) | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/2 |  |  | CAST IRON | 12 | 1404 | 2240 | [9 empty] | ODP | 4775 |  | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 25.923 | 73.000 | [5 empty] | 19-5-1434 | THOMAS 71 SIZE 512 | DRIVE-FIXED |  |  |  | Yes | [9 empty] | 3.4370 | 3.4355 |  | 0.8750 X 0.4375 | 131 1/2 | 27 7/8 | 534 |  | Yes | Ambient Temp F=90 | Size=6600; Design=1910; Arrangement=781,100.0 PCT; % Width=100.0; Discharge=TH; Rotation=ROT CCW; CFM=123323; SP=11.26; BHP=286.0; RPM=1185; Max Temp F=500; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Wheel Material=CAST IRON; Hub=19-5-1434; Coupling=THOMAS 71 SIZE 512; Blades=12; Shaft Dia=6 3/4; Brg Centers=105 13/16; Critical Speed RPM=1899; BX=93.75; STB=9.62; OH=20.02; STH=4.94; Bearing Size=3 7/16; Bearing Series=6800; Motor Enclosure=ODP; Drive=DRIVE-FIXED | Open
411306 | HDX | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | SN411306 3154 ID PAN | 3600 | 3154 |  |  | ARR 781,100.0 PCT, DISCH TH, ROT CCW, BOX 0 | 100.0 | TH | CCW | 6600 | 123323 | 11.26 | 286.0 | 1185 | 90 | 500 | 0.0419 | 300.0 | 1303 | 24293 | 6 3/4 | 105 13/16 | 1899 |  |  |  | 9.62 |  | 4.94 | 7/16 | Link Belt Series 6800 | 400000 | FIXED | 1899 | FLOAT | 795 | 0 |  | 1356 |  | 0.17 | 0.58 |  |  | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A572 X-TEN | 1/2 |  |  | CAST IRON | 12 | 1404 | 2240 | [9 empty] | ODP | 4250 |  | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 25.923 | 73.000 |  |  |  | 23682 | 248175 | 19-5-1434 | THOMAS 71 SIZE 512, BORE 3 7/16 NOT INCL. | DRIVE-FIXED |  |  |  | Yes | [9 empty] | 3.4370 | 3.4355 |  | 0.8750 X 0.4375 | 131 1/2 | 27 7/8 | 1177 |  | Yes | Ambient Temp F=90 | Size=3600; Design=3154; Arrangement=ARR 781,100.0 PCT, DISCH TH, ROT CCW, BOX 0; % Width=100.0; Discharge=TH; Rotation=CCW; CFM=123323; SP=11.26; BHP=286.0; RPM=1185; Max Temp F=500; Effective Wheel Dia=6600; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Wheel Material=CAST IRON; Hub=19-5-1434; Coupling=THOMAS 71 SIZE 512, BORE 3 7/16 NOT INCL.; Blades=12; Shaft Dia=6 3/4; Brg Centers=105 13/16; Critical Speed RPM=1899; STB=9.62; STH=4.94; Bearing Size=7/16; Bearing Series=Link Belt Series 6800; Motor Enclosure=ODP; Drive=DRIVE-FIXED | Open
411479 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 411479 | 4900 | 6195 |  |  | 4S | 105.0 | TH | CW | 46 9/16 | 36073 | 8.00 | 59.6 | 1190 | 90 | 115 | 0.0660 | 100.0 | 1200 | 14624 | [8 empty] | 2.94 | [15 empty] | ASTM A6 XF-100 | 5/16 | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 5/8 |  |  |  | 10 | 2126 | 4140 | 779 | 192 | 1740 | 6.10 | 7.32 |  |  | 444T |  | TEFC | 1893 | 1/4 A572 X-TEN | SK-9-236 MED PRESSURE, 30 IN. CENTERS | 13.275 |  | Not included |  | Yes | 5294 | 65263 | 19-5-219 |  | Motor mounted |  |  | Yes |  | Yes | [5 empty] | 3 3/8 | [12 empty] | Size=4900; Design=6195; Arrangement=4S; % Width=105.0; Discharge=TH; Rotation=CW; CFM=36073; SP=8.00; BHP=59.6; RPM=1190; Max Temp F=115; Effective Wheel Dia=46 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=5/16; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/8; Hub=19-5-219; Blades=10; STH=2.94; Motor Frame=444T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
411480 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 411480 | 3612 | 6195 |  |  | 4S | 100.0 | TH | CCW | 34 11/16 | 22335 | 9.00 | 43.7 | 1780 | 90 | 115 | 0.0660 | 60.0 | 1800 | 16340 | [8 empty] | 2.25 | [15 empty] | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A572 X-TEN | 1/4 |  |  |  | 10 | 2059 | 3730 | 236 | 133 | 263 | 4.74 | 6.13 |  |  | 364T |  | TEFC | 1043 | 7 GA A607 X-TEN | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 7.216 |  | Not included |  | Included | 2514 | 26964 | 19-5-11 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 3/8 | [12 empty] | Size=3612; Design=6195; Arrangement=4S; % Width=100.0; Discharge=TH; Rotation=CCW; CFM=22335; SP=9.00; BHP=43.7; RPM=1780; Max Temp F=115; Effective Wheel Dia=34 11/16; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=19-5-11; Blades=10; STH=2.25; Motor Frame=364T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
411483 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN 7-24.txt |  |  | 411483 | 4014 | 1904 |  | PACKAGED FORCED DRAFT FAN | 4S1 | 95.0 | DB | CW | 44 1/4 | 29453 | 19.67 | 115.5 | 1780 | 164 | 180 | 0.0607 | 150.0 | 1800 | 20864 | [8 empty] | 2.50 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 5/16 |  |  |  | 10 | 2113 | 2640 | 313 | 292 | 517 | 4.81 | 6.38 |  |  | 445T |  | TEFC | 2231 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 8.669 |  | Not included |  |  |  |  | 19-5-16 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 3 3/8 | [6 empty] | 73 | 15 9/16 | 1 | SK-19-72 |  | Ambient Temp F=90 | Size=4014; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S1; % Width=95.0; Discharge=DB; Rotation=CW; CFM=29453; SP=19.67; BHP=115.5; RPM=1780; Max Temp F=180; Effective Wheel Dia=44 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=5/16; Hub=19-5-16; Blades=10; STH=2.50; Motor Frame=445T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
411484 | HD-PFD-IAF | CHECK VISION | pdf_vision | QT RUN 11-10-23.pdf |  |  | 411484, 411490 | 3612 | 1903 |  | PACKAGED FORCED DRAFT FAN | 451 | 45.0 | DB | CW | 38 5/16 | 11011 | 14.36 | 34.3 | 1770 | 90 | 130 | 0.0701 | 40.0 | 1800 | 18060 | [8 empty] | 2.25 | [15 empty] | ASTM A1011-HSLAS | 0.060 (16) | ASTM A1011-HSLAS | 0.135 (10) | ASTM CQ HRS A36 | 1/4 |  |  | CAST IRON | 10 | 2721 | 3400 | 200 | 173 | 208 | 3.45 | 6.13 |  |  | 324T |  |  | 550 | 1/4 C.Q. HRS | SK-9-236 | 5.809 |  | Not included |  |  |  |  | 19-5-16 BORE 2 1/8 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 1/8 | [6 empty] | 65 3/4 | 13 15/16 | 1 |  |  | Ambient Temp F=90; Blade Count=10; Wheel Weight=200; Thrust=173; WR2 Weight=208; Outlet N x A=20 1/8 IN. X 41 9/16 IN.; Box B x C=65 3/4 IN. X 13 15/16 IN.; Base=324T; Motor Type=FR MOTOR; Motor Mounting=INCLUDED; Motor Weight=550; Split Housing and Box=1/4 C.Q. HRS; Outlet Damper Torque=491; Outlet Damper Area=5.809; Axles=52.0 L, 11 IN.; Damper Frame=A36; Damper Frame Thickness=1/4; Automatic Control=DIRECT COUPLED; Master Axle Location=1 | Size=3612; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=451; % Width=45.0; Discharge=DB; Rotation=CW; CFM=11011; SP=14.36; BHP=34.3; RPM=1770; Max Temp F=130; Effective Wheel Dia=38 5/16; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Wheel Material=CAST IRON; Hub=19-5-16 BORE 2 1/8; Blades=10; STH=2.25; Motor Frame=324T; Drive=Motor mounted | Open
411484 | HD-PFD-IAF | OK | cbc_qt_run_text | 411484 QUOTE RUN.txt |  |  | 411484 | 3612 | 1903 |  | PACKAGED FORCED DRAFT FAN | 4S1 | 45.0 | DB | CW | 38 5/16 | 11011 | 14.36 | 34.3 | 1770 | 90 | 130 | 0.0701 | 40.0 | 1800 | 18060 | [8 empty] | 2.25 | [15 empty] | ASTM A1011-HSLAS | 0.060 (16) | ASTM A1011-HSLAS | 0.135 (10) | ASTM CQ HRS A36 | 1/4 |  |  |  | 10 | 2721 | 3400 | 200 | 173 | 208 | 3.45 | 6.13 |  |  | 324T |  |  | 550 | 1/4 C.Q. HRS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 5.809 |  | Not included |  |  |  |  | 19-5-16 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 1/8 | [6 empty] | 65 3/4 | 13 15/16 | 1 |  |  | Ambient Temp F=90 | Size=3612; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S1; % Width=45.0; Discharge=DB; Rotation=CW; CFM=11011; SP=14.36; BHP=34.3; RPM=1770; Max Temp F=130; Effective Wheel Dia=38 5/16; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Hub=19-5-16; Blades=10; STH=2.25; Motor Frame=324T; Drive=Motor mounted | Open
411485 | HD-PFD-IAF | OK | cbc_qt_run_text | 411485 QUOTE RUN.txt |  |  | 411485 | 3300 | 1903 |  | PACKAGED FORCED DRAFT FAN | 4S1 | 95.0 | DB | CCW | 34 5/8 | 13690 | 13.15 | 35.4 | 1770 | 90 | 130 | 0.0687 | 40.0 | 1800 | 16328 | [8 empty] | 2.12 | [15 empty] | ASTM A1011-HSLAS | 0.060 (16) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 10 | 2134 | 2670 | 173 | 115 | 146 | 4.49 | 6.01 |  |  | 324T |  |  | 550 | 1/4 C.Q. HRS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 5.837 |  | Not included |  |  |  |  | 19-5-16 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 1/8 | [6 empty] | 59 1/2 | 12 5/8 | 1 |  |  | Ambient Temp F=90 | Size=3300; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S1; % Width=95.0; Discharge=DB; Rotation=CCW; CFM=13690; SP=13.15; BHP=35.4; RPM=1770; Max Temp F=130; Effective Wheel Dia=34 5/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=19-5-16; Blades=10; STH=2.12; Motor Frame=324T; Drive=Motor mounted | Open
411488 | HDX | OK | pdf_vision | QT RUN-CO#1.pdf |  |  | SN#411488 | 4900 | 6105 |  |  | 8S | 95.0 | PCT,DISCH DB ,ROT CW | CW | 51 7/16 | 50982 | 28.90 | 277.0 | 1780 | 137 | 180 | 0.0638 | 350.0 | 1800 | 24245 | 3 15/16 | 16 | 3365 | 40 11/16 | 13.34 | 1/4 | 1/8 |  | 2.94 | 3 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -383 | FLOAT | 1182 | 0 | 1344 | 1932 |  | 0.39 | 0.29 |  |  | ASTM A6 XF-100 | 5/16 | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 3/8 |  |  | CAST STEEL | 10 | 1932 | 2920 | [9 empty] | ODP | 3875 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 12.790 |  | Included | 3.00 | Included | 9639 | 95634 | 19-5-219 | FAIK T10, SIZE 1100T, BORE 3.438 | Direct |  | Required |  | Yes | [6 empty] | 3 11/16 |  |  | 3.4370 | 3.4355 | 3.4375 | 0.8750 X 0.4375 |  |  |  | SK-19-72 | Yes | Ambient Temp F=70; Wheel Hub Nominal Bore=3.6875; Wheel Hub Max Bore=3.6890; Wheel Hub Min Bore=3.6880; Shrink Fit Max Shaft Dia=3.6920; Shrink Fit Min Shaft Dia=3.6910; Nominal Shaft Dia At Fan Shaft Half Coupling=3.4375; Max Shaft Diameter At Fan Shaft Half Coupling=3.4370; Min Shaft Diameter At Fan Shaft Half Coupling=3.4355; Keyway Dimensions=0.8750 X 0.4375 | Size=4900; Design=6105; Arrangement=8S; % Width=95.0; Discharge=PCT,DISCH DB ,ROT CW; Rotation=CW; CFM=50982; SP=28.90; BHP=277.0; RPM=1780; Max Temp F=180; Effective Wheel Dia=51 7/16; Blade Material=ASTM A6 XF-100; Blade Gauge=5/16; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Wheel Material=CAST STEEL; Hub=19-5-219; Coupling=FAIK T10, SIZE 1100T, BORE 3.438; Blades=10; Shaft Dia=3 15/16; Brg Centers=16; Critical Speed RPM=3365; BX=1/4; STB=1/8; OH=13.34; STH=2.94; Bearing Size=3 15/16; Bearing Series=LINK BELT SERIES 6800; Motor Enclosure=ODP; Drive=Direct | Open
411490 | HD-PFD-IAF | OK | cbc_qt_run_text | 411490 QUOTE RUN.txt |  |  | 411490 | 3612 | 1903 |  | PACKAGED FORCED DRAFT FAN | 4S1 | 45.0 | DB | CW | 38 5/16 | 11011 | 14.36 | 34.3 | 1770 | 90 | 130 | 0.0701 | 40.0 | 1800 | 18060 | [8 empty] | 2.25 | [15 empty] | ASTM A1011-HSLAS | 0.060 (16) | ASTM A1011-HSLAS | 0.135 (10) | ASTM CQ HRS A36 | 1/4 |  |  |  | 10 | 2721 | 3400 | 200 | 173 | 208 | 3.45 | 6.13 |  |  | 324T |  |  | 550 | 1/4 C.Q. HRS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 5.809 |  | Not included |  |  |  |  | 19-5-16 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 1/8 | [6 empty] | 65 3/4 | 13 15/16 | 1 |  |  | Ambient Temp F=90 | Size=3612; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S1; % Width=45.0; Discharge=DB; Rotation=CW; CFM=11011; SP=14.36; BHP=34.3; RPM=1770; Max Temp F=130; Effective Wheel Dia=38 5/16; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Hub=19-5-16; Blades=10; STH=2.25; Motor Frame=324T; Drive=Motor mounted | Open
411508 | GENERAL LINE | OK | cbc_qt_run_text | QT Run.txt |  |  | 411508 | 4900 | 6195 |  |  | 8S | 115.0 | TH | CCW | 46 9/16 | 55331 | 20.00 | 219.6 | 1768 | 80 | 608 | 0.0740 | 250.0 | 1800 | 21936 | 4 7/16 | 16 | 3205 | 43 5/16 | 15.39 | 26 3/16 | 11 |  | 2.94 | 4 7/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -552 | FLOAT | 1515 | 0 | 1617 | 1800 | 1045 STEEL | 0.31 | 0.15 | 35 3/8 |  | ASTM A6 XF-100 | 5/16 | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 1/2 |  |  |  | 10 | 1886 | 3170 | [7 empty] | 449T |  |  | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 13.711 |  |  |  | Included | 8281 | 89228 | 19-5-219 | FALK T10 | Direct |  |  | Yes | Yes | Yes | [5 empty] | 4 3/16 |  |  | 3.4370 | 3.4355 | 3.4375 | 0.8750 X 0.4375 |  |  |  | SK-19-72 | Yes | Ambient Temp F=90; Discharge Height (A)=55 13/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=36 1/2; Base Width (F)=66 1/4; Shaft Height (H)=46 7/16; Total Vert Height (TV)=104 1/4; Max Right of CL to Hsg (RH)=48 1/8; Max Left of CL to Disch (LH)=36 1/2; Base Flange to CL (D)=99 13/16; Drive End of Shaft to CL (K)=53 3/16; Mtg Flange to CL (LR)=19 19/32 | Size=4900; Design=6195; Arrangement=8S; % Width=115.0; Discharge=TH; Rotation=CCW; CFM=55331; SP=20.00; BHP=219.6; RPM=1768; Max Temp F=608; Effective Wheel Dia=46 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=5/16; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Hub=19-5-219; Coupling=FALK T10; Blades=10; Shaft Dia=4 7/16; Brg Centers=16; Critical Speed RPM=3205; BX=26 3/16; STB=11; OH=15.39; STH=2.94; Bearing Size=4 7/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=35 3/8; Motor Frame=449T; Drive=Direct | Open
411602 | HDX | OK | pdf_vision | QT RUN.pdf |  |  | 365-23-524RP | 4800 | 2300B |  |  | 8S | 55.0 | UB | CCW | 48 | 12000 | 22.00 | 56.6 | 1750 | 185 | 185 | 0.0370 | 75.0 | 1750 | 21991 | 2 15/16 | 12 1/2 | 3549 | 32 1/8 | 9.50 | 10 1/2 | 6 15/16 |  | 1.94 | 2 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -312 | FLOAT | 838 | 0 | 837 | 2571 |  | 0.30 | 0.15 |  |  | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 3/8 |  |  | CAST STEEL | 11 | 2571 | 9110 | [7 empty] | 365T |  | ODP | 920 | 7 GA C.O. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 1.523 |  |  |  |  | 3336 | 49009 | 2 11/16 | FALK G20 | Direct |  |  |  | Yes | Yes | [5 empty] | 2 11/16 | [10 empty] | Yes | Ambient Temp F=90; Coupling Size=1015G; Coupling Bore=2.188 | Size=4800; Design=2300B; Arrangement=8S; % Width=55.0; Discharge=UB; Rotation=CCW; CFM=12000; SP=22.00; BHP=56.6; RPM=1750; Max Temp F=185; Effective Wheel Dia=48; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Wheel Material=CAST STEEL; Hub=2 11/16; Coupling=FALK G20; Blades=11; Shaft Dia=2 15/16; Brg Centers=12 1/2; Critical Speed RPM=3549; BX=10 1/2; STB=6 15/16; OH=9.50; STH=1.94; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=365T; Motor Enclosure=ODP; Drive=Direct | Open
411631 | GENERAL LINE | OK | d64_wheel_construction | 411631_D64 Wheel Construction (Outer Ring) 345-20-1754.xlsx | [103 empty] | Fan Size=182; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=50000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.25 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=182; Outer Ring Thickness=0.25; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=50000 | Open
411674 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 411674 | 4900 | 6195 |  |  | 4S | 115.0 | UB | CW | 46 9/16 | 64000 | 18.05 | 260.6 | 1770 | 70 | 70 | 0.0750 | 300.0 | 1800 | 21936 | [8 empty] | 2.94 | [15 empty] | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 3/8 |  |  |  | 10 | 1805 | 2640 | 588 | 432 | 1342 | 7.26 | 7.32 |  |  | 449T |  |  | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 13.711 |  | Not included |  | Yes | 6894 | 58135 | 19-5-289 |  | Motor mounted |  |  | Yes | [7 empty] | 3 3/8 | [9 empty] | SK-19-72 |  | Ambient Temp F=70 | Size=4900; Design=6195; Arrangement=4S; % Width=115.0; Discharge=UB; Rotation=CW; CFM=64000; SP=18.05; BHP=260.6; RPM=1770; Max Temp F=70; Effective Wheel Dia=46 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Hub=19-5-289; Blades=10; STH=2.94; Motor Frame=449T; Drive=Motor mounted | Open
411733 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 411733 | 4900 | 6195 |  |  | 4S | 100.0 | UB | CCW | 46 9/16 | 45000 | 24.00 | 208.9 | 1770 | 70 | 70 | 0.0720 | 250.0 | 1800 | 24130 | [8 empty] | 2.94 | [15 empty] | ASTM A6 XF-100 | 3/16 | ASTM A572 X-TEN | 3/16 | ASTM A572 X-TEN | 5/16 |  |  |  | 10 | 2046 | 2560 | 486 | 432 | 1012 | 6.30 | 7.32 |  |  | 449T |  |  | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 13.033 |  | Not included |  | Yes | 6776 | 58695 | 19-5-219 |  | Motor mounted |  |  | Yes |  | Yes | [5 empty] | 3 3/8 | [9 empty] | SK-19-72 |  | Ambient Temp F=70 | Size=4900; Design=6195; Arrangement=4S; % Width=100.0; Discharge=UB; Rotation=CCW; CFM=45000; SP=24.00; BHP=208.9; RPM=1770; Max Temp F=70; Effective Wheel Dia=46 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=3/16; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=19-5-219; Blades=10; STH=2.94; Motor Frame=449T; Drive=Motor mounted | Open
411814 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.txt |  |  | 411814 | 2412 | 1902 |  |  | 4S | 90.0 | UB | CCW |  | 10000 | 24.00 | 45.9 | 3414 | 70 | 100 | 0.0750 | 60.0 | 3600 | 23091 | [8 empty] | 1.62 | [15 empty] | ASTM A240 316L SS | 0.075 (14) | ASTM A240 316L SS | 3/16 | ASTM A240 316L SS | 1/4 |  |  |  | 10 | 3611 | 6010 | 113 | 122 | 57 | 3.33 | 3.88 |  |  | 364TS |  | TEFC | 1043 | 3/16 A240 316L SS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 3.153 |  | Not included |  | Yes |  |  | 19-5- |  | Motor mounted |  |  | Yes |  | Yes | [5 empty] | 1 7/8 | [11 empty] | Ambient Temp F=90 | Size=2412; Design=1902; Arrangement=4S; % Width=90.0; Discharge=UB; Rotation=CCW; CFM=10000; SP=24.00; BHP=45.9; RPM=3414; Max Temp F=100; Blade Material=ASTM A240 316L SS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A240 316L SS; Sideplate Gauge=3/16; Backplate Material=ASTM A240 316L SS; Backplate Gauge=1/4; Hub=19-5-; Blades=10; STH=1.62; Motor Frame=364TS; Motor Enclosure=TEFC; Drive=Motor mounted | Open
411820 | HDX | CHECK VISION | pdf_vision | QT RUN 411820.pdf |  |  | SN411820 | 4412 | 5800 |  |  | 9H | 100.0 | UB | CCW | 48 7/8 | 12150 | 50.60 | 192.3 | 2037 | 90 | 140 | 0.0766 | 200.0 | 2137 | 27344 | 3 3/16 | 14 | 6061 | 34 7/8 | 7.56 | 3/8 | 11 7/8 |  | 2.06 | 3 3/16 | LINK BELT SERIES 6800 | 68141 | FLOAT | 3706 | FIXED | 1066 | 319 |  | 2427 |  | 0.35 | 0.80 |  |  | ASTM A1011 CS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A36 | 3/8 |  |  | CAST STEEL | 10 | 2427 | [6 empty] | 7.5 | 6.1 | 447 | Z | ODP | 2280 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 19 IN. CENTERS | 2.591 |  |  |  | Included | 5461 | 57392 | 2.9375 |  | Belt |  |  |  | Yes | Yes | [5 empty] | 2 15/16 | [10 empty] | Yes | Ambient Temp F=90 | Size=4412; Design=5800; Arrangement=9H; % Width=100.0; Discharge=UB; Rotation=CCW; CFM=12150; SP=50.60; BHP=192.3; RPM=2037; Max Temp F=140; Effective Wheel Dia=48 7/8; Blade Material=ASTM A1011 CS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A36; Backplate Gauge=3/8; Wheel Material=CAST STEEL; Hub=2.9375; Blades=10; Shaft Dia=3 3/16; Brg Centers=14; Critical Speed RPM=6061; BX=3/8; STB=11 7/8; OH=7.56; STH=2.06; Bearing Size=3 3/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=447; Motor Position=Z; Motor Enclosure=ODP; Drive=Belt | Open
411821 | HDX | CHECK VISION | pdf_vision | QT RUN 411821.pdf |  |  | SN411821 | 4412 | 5800 |  |  | 9H | 100.0 | UB | CW | 48 7/8 | 11550 | 50.60 | 192.3 | 2037 | 59 | 140 | 0.0766 | 200.0 | 2137 | 27344 | 3 3/16 | 14 | 6061 | 34 7/8 | 7.56 | 13 3/8 | 11 7/8 | MI.5 | 2.06 | 3 3/16 | LINK BELT SERIES 6800 | 68141 | FLOAT | 3706 | FIXED | 1066 | 319 |  | 2427 |  | 0.35 | 0.80 |  |  | ASTM A1011 CS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM CO HRS A36 | 3/8 |  |  | CAST STEEL | 10 | 2427 | [6 empty] | 7.5 | 6.1 | 447 | W |  | 2280 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 19 IN. CENTERS | 2.591 |  |  |  | Included | 5461 | 57392 | 2 9375 |  | Belt |  |  |  | Yes | Yes | [5 empty] | 2 15/16 | [10 empty] | Yes | Ambient Temp F=90 | Size=4412; Design=5800; Arrangement=9H; % Width=100.0; Discharge=UB; Rotation=CW; CFM=11550; SP=50.60; BHP=192.3; RPM=2037; Max Temp F=140; Effective Wheel Dia=48 7/8; Blade Material=ASTM A1011 CS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM CO HRS A36; Backplate Gauge=3/8; Wheel Material=CAST STEEL; Hub=2 9375; Blades=10; Shaft Dia=3 3/16; Brg Centers=14; Critical Speed RPM=6061; BX=13 3/8; STB=11 7/8; OH=7.56; STH=2.06; Bearing Size=3 3/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=447; Motor Position=W; Drive=Belt | Open
411829 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN A4.txt |  |  | 411829 | 4014 | 1903 |  | PACKAGED FORCED DRAFT FAN | 8S | 60.0 | DB | CCW | 42 1/4 | 16851 | 17.94 | 62.5 | 1770 | 125 | 125 | 0.0662 | 75.0 | 1800 | 19916 | 2 7/16 | 14 | 4689 | 29 1/2 | 7.21 | 15 3/16 | 7 | 39 | 2.50 | 2 7/16 | LINK BELT SERIES 300 | 400000 | FIXED | -75 | FIXED | 338 | 255 | 320 | 1995 | 1045 STEEL | 0.28 | 0.25 |  |  | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 1/4 |  |  |  | 10 | 2234 | 2790 | [7 empty] | 365T |  | TEFC | 1150 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 7.596 |  |  |  | Yes |  |  | 19-5-1057 | FALK T10 | Direct |  |  |  |  | Yes | [7 empty] | Q1 BUSHING 2 7/16 | [7 empty] | SK-19-72 | Yes | Ambient Temp F=90 | Size=4014; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=8S; % Width=60.0; Discharge=DB; Rotation=CCW; CFM=16851; SP=17.94; BHP=62.5; RPM=1770; Max Temp F=125; Effective Wheel Dia=42 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Hub=19-5-1057; Coupling=FALK T10; Blades=10; Shaft Dia=2 7/16; Brg Centers=14; Critical Speed RPM=4689; BX=15 3/16; STB=7; OH=7.21; STH=2.50; Bearing Size=2 7/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=365T; Motor Enclosure=TEFC; Drive=Direct | Open
412000 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.txt |  |  | 412000 | 2412 | 1903 |  | PACKAGED FORCED DRAFT FAN | 4S | 95.0 | TH | CW | 25 3/4 | 4922 | 1.65 | 2.0 | 1160 | 110 | 125 | 0.0697 | 5.0 | 1200 | 8082 | [8 empty] | 1.62 | [15 empty] | ASTM A1011-HSLAS | 0.048 (18) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 10 | 3918 | 4900 | 79 | 16 | 39 | 3.13 | 4.12 |  |  | 215T |  | TEFC | 200 | 10 GA C.Q. HRS | SK-9-236 LOW PRESSURE, 36 IN. CENTERS | 3.225 |  | Not included |  | Yes |  |  | 19-5-1056 |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q1 BUSHING 1 3/8 | [9 empty] | Ambient Temp F=90 | Size=2412; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S; % Width=95.0; Discharge=TH; Rotation=CW; CFM=4922; SP=1.65; BHP=2.0; RPM=1160; Max Temp F=125; Effective Wheel Dia=25 3/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.048 (18); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=19-5-1056; Blades=10; STH=1.62; Motor Frame=215T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
412061 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 412061 | 4412 | 6195 |  |  | 8S | 105.0 | TH | CCW | 42 1/4 | 48000 | 14.00 | 145.2 | 1785 | 70 | 100 | 0.0750 | 150.0 | 1800 | 19922 | 3 7/16 | 14 | 3695 | 35 5/8 | 10.92 | 20 1/8 | 9 3/8 | 94 | 2.81 | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -332 | FLOAT | 987 | 0 | 964 | 1873 | 1045 STEEL | 0.24 | 0.17 | 31 1/8 |  | ASTM A572 X-TEN | 5/16 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 3/8 |  |  |  | 10 | 1873 | 3550 | [7 empty] | 445T |  |  | 1785 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 10.942 |  | Included |  | Included | 5870 | 51909 | 19-5-219 | FALK T10 | Direct |  |  |  |  | Yes | [5 empty] | 3 7/16 |  |  | 3.4370 | 3.4355 | 3.4375 | 0.8750 X 0.4375 |  |  |  |  | Yes | Ambient Temp F=70; Discharge Height (A)=50 5/8; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=33 1/4; Base Width (F)=60 1/2; Shaft Height (H)=44 13/16; Total Vert Height (TV)=97 7/16; Max Right of CL to Hsg (RH)=43 11/16; Max Left of CL to Disch (LH)=33 1/4; Base Flange to CL (D)=80 7/8; Drive End of Shaft to CL (K)=43 1/2; Mtg Flange to CL (LR)=17 13/16 | Size=4412; Design=6195; Arrangement=8S; % Width=105.0; Discharge=TH; Rotation=CCW; CFM=48000; SP=14.00; BHP=145.2; RPM=1785; Max Temp F=100; Effective Wheel Dia=42 1/4; Blade Material=ASTM A572 X-TEN; Blade Gauge=5/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Hub=19-5-219; Coupling=FALK T10; Blades=10; Shaft Dia=3 7/16; Brg Centers=14; Critical Speed RPM=3695; BX=20 1/8; STB=9 3/8; OH=10.92; STH=2.81; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=31 1/8; Motor Frame=445T; Drive=Direct | Open
412244 | HDX | OK | pdf_vision | QT RUN.pdf |  |  | SN#412244 | 2700 | 1902 |  | CHICAGO BLOWER CORP. | 8S | 70.0 | CCW | ROT CCW | 3834 | 13500 | 13.50 | 40.0 | 3540 | 280 | 280 | 0.0430 | 40.0 | 3540 | 25023 | 1 15/16 | 12 | 5509 | 26 11/16 | 5.88 | 11 | 1 1/8 | 0.5000 X 0.2500 | 1.69 | 1 15/16 | LINK BELT SERIES 300 | 400000 | FIXED | -25 | FIXED | 164 | 65 | 61 | 3834 | 1045 STEEL | 0.31 | 0.14 |  |  | ASTM A1011-HSLAS | 0.048 (18) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A572 X-TEN | 1/4 |  |  |  | 10 | 3834 | 5700 | [7 empty] | 324TS |  |  | 550 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS |  |  |  |  | Yes | 1578 | 33773 | 19-5-27 | FALK G20, SIZE 1015G | Direct |  | Required |  | Yes | Yes | [5 empty] | 1 11/16 |  |  | 1.9370 | 1.9360 | 1.9375 | 0.5000 X 0.2500 |  |  |  |  | Yes | Discharge TH=DISCH TH; DUCT=70 F | Size=2700; Design=1902; Fan Type=CHICAGO BLOWER CORP.; Arrangement=8S; % Width=70.0; Discharge=CCW; Rotation=ROT CCW; CFM=13500; SP=13.50; BHP=40.0; RPM=3540; Max Temp F=280; Effective Wheel Dia=3834; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.048 (18); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=19-5-27; Coupling=FALK G20, SIZE 1015G; Blades=10; Shaft Dia=1 15/16; Brg Centers=12; Critical Speed RPM=5509; BX=11; STB=1 1/8; OH=5.88; STH=1.69; Bearing Size=1 15/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=324TS; Drive=Direct | Open
412244 | HDX | OK | pdf_vision | QT RUN.pdf |  |  | 27,000 | 27,000 | 1902 |  |  | 8S | 68.0 | OUTLET |  | 1.938 | 13500 | 13.50 | 39.0 | 3540 | 280 | 70 | .0430 |  | 3905 | 25023 | 1.938 | 12.00 | 5451 | 28.64 | 6.08 | 5.88 |  |  |  | 1.9375 | LINK BELT P300 | 1000000 | [12 empty] | ASTM A606 CORTEN | .048 (18) | ASTM A606 CORTEN | .105 (12) | ASTM A242 CORTEN | .250 |  |  | CAST STEEL | [23 empty] | 19-5-27 | [24 empty] | Housing Material=C.0. | Backplate Material=ASTM A242 CORTEN; Blade Material=ASTM A606 CORTEN; Housing Material=C.0.; Sideplate Material=ASTM A606 CORTEN; Wheel Material=CAST STEEL; Backplate Gauge=.250; Blade Gauge=.048 (18); Sideplate Gauge=.105 (12); Bearing L10 Hr=1000000; Bearing Series=LINK BELT P300; Bearing Size=1.9375; Shaft Dia=1.938 | Open
412316 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN REVISION 5-8.txt |  |  | 412316 | 300 | 51A | 3 |  | 3 |  |  |  |  | 18000 | 12.55 | 47.3 | 2400 |  |  |  |  | 2768 | 18300 | 2 3/16 | 27 | 5157 |  |  |  | 10.09 | 47 | 2.62 | 2 3/16 | LINK BELT SERIES 22400 | 377282 | FIXED | 675 | FIXED | 91 | 0 | 55 | 2768 | 1045 STEEL | 0.57 | 0.80 |  |  | ASTM A1008 HSLAS | 0.060 (16) | ASTM A1011 CS | 0.075 (14) | ASTM A1011 CS | 0.135 (10) |  |  |  | 8 | 2768 | 6330 | [5 empty] | 8.4 | [14 empty] | 4-5-15 |  | Belt | Required | [9 empty] | 2 3/16 | [11 empty] | Ambient Temp F=90 | Size=300; Design=51A; Arrangement=3; Class=3; CFM=18000; SP=12.55; BHP=47.3; RPM=2400; Blade Material=ASTM A1008 HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.075 (14); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.135 (10); Hub=4-5-15; Blades=8; Shaft Dia=2 3/16; Brg Centers=27; Critical Speed RPM=5157; STB=10.09; STH=2.62; Bearing Size=2 3/16; Bearing Series=LINK BELT SERIES 22400; Drive=Belt | Open
412337 | GENERAL LINE | OK | cbc_qt_run_text | 368-23-3309 quote run.txt |  |  | 412337 | 20 | 36 | 1 |  | 4S | 110.0 | TH | CW |  | 7000 | 2.00 | 5.2 | 1750 | 70 | 135 | 0.0740 | 7.5 | 1800 | 10169 | [8 empty] | 2.04 | [15 empty] | ASTM A240 304L SS | 0.060 (16) | ASTM A240 304L SS | 0.105 (12) | ASTM A240 304L SS | 0.105 (12) |  |  |  | 8 | 2527 | 7780 | 46 | 18 | 18 | 4.48 | 5.67 | [15 empty] | 4-5-145 |  |  |  |  | Yes |  | Yes | [5 empty] | 1 3/8 | [11 empty] | Ambient Temp F=90 | Size=20; Design=36; Arrangement=4S; % Width=110.0; Discharge=TH; Rotation=CW; Class=1; CFM=7000; SP=2.00; BHP=5.2; RPM=1750; Max Temp F=135; Blade Material=ASTM A240 304L SS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A240 304L SS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A240 304L SS; Backplate Gauge=0.105 (12); Hub=4-5-145; Blades=8; STH=2.04 | Open
412477 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 412477 | 6000 | 6195 |  |  | 9H1 | 100.0 | UB | CW | 57 | 70000 | 16.00 | 230.6 | 1272 | 70 | 70 | 0.0750 | 250.0 | 1272 | 18982 | 3 15/16 | 20 | 2267 | 49 1/8 | 12.27 | 25 3/8 | 14 7/8 | 170 | 4.12 | 3 15/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 4141 | FIXED | 1114 | 485 | 2835 | 1453 | 1045 STEEL | 0.33 | 0.66 | 41 1/4 | 39 3/4 | ASTM A6 XF-100 | 3/16 | ASTM A572 X-TEN | 3/16 | ASTM A572 X-TEN | 1/2 |  |  |  | 10 | 1459 | 2000 | [5 empty] | 12.0 | 7.3 | 449T | W |  | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 19.551 |  | Included |  |  | 11806 | 108437 | 19-5-17 |  | Belt |  |  | Yes |  | Yes | [5 empty] | 3 15/16 | [6 empty] | 108 | 22 3/4 | 1 |  | Yes | Ambient Temp F=70; Discharge Height (A)=68 1/4; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=3; Discharge Flange to CL (E)=54; Unitary Base to CL (RB)=93 7/16; Motor CL to Fan CL (RM)=71 9/16; Inlet Box Width (B)=108; Inlet Box Length To Cl (J)=53 1/2; Shaft Height (H)=67 1/4; Total Vert Height (TV)=121 1/4; Max Right of CL to Hsg (RH)=57; Max Left of CL to Disch (LH)=71 1/4; Mounting Channel (MA)=2 1/4; Base Flange to CL (D)=51 1/4; Drive End of Shaft to CL (K)=60 1/4; Box Cl To Hsg Cl (P)=46 3/4; Box Width Os (C)=22 3/4; Mtg Flange to CL (LR)=61 1/8 | Size=6000; Design=6195; Arrangement=9H1; % Width=100.0; Discharge=UB; Rotation=CW; CFM=70000; SP=16.00; BHP=230.6; RPM=1272; Max Temp F=70; Effective Wheel Dia=57; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=3/16; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Hub=19-5-17; Blades=10; Shaft Dia=3 15/16; Brg Centers=20; Critical Speed RPM=2267; BX=25 3/8; STB=14 7/8; OH=12.27; STH=4.12; Bearing Size=3 15/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=41 1/4; Base to CL (F)=39 3/4; Motor Frame=449T; Motor Position=W; Drive=Belt | Open
412502 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN (USED FOR STATIC AND DYNAMIC LOADS ONLY).txt |  |  | 412502 | 4014 | 6195 |  |  | 8S | 100.0 | TH | CW | 38 1/4 | 37531 | 5.50 | 61.6 | 1770 | 110 | 110 | 0.0671 | 75.0 | 1800 | 18019 | 2 3/16 | 14 | 2366 | 30 13/16 | 9.27 | 17 1/16 | 6 3/4 | 33 | 2.50 | 2 3/16 | LINK BELT SERIES 300 | 400000 | FIXED | -173 | FIXED | 523 | 197 | 457 | 1832 | 1045 STEEL | 0.48 | 0.34 |  |  | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 |  |  |  | 10 | 2035 | 3110 | [7 empty] | 365T |  |  | 920 | 7 GA C.Q. HRS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 8.828 |  |  |  | Yes | 3065 | 47021 | 19-5-11 | FALK T10 | Direct | Required |  |  |  | Yes | [5 empty] | 2 3/16 | [10 empty] | Yes | Ambient Temp F=70 | Size=4014; Design=6195; Arrangement=8S; % Width=100.0; Discharge=TH; Rotation=CW; CFM=37531; SP=5.50; BHP=61.6; RPM=1770; Max Temp F=110; Effective Wheel Dia=38 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=19-5-11; Coupling=FALK T10; Blades=10; Shaft Dia=2 3/16; Brg Centers=14; Critical Speed RPM=2366; BX=17 1/16; STB=6 3/4; OH=9.27; STH=2.50; Bearing Size=2 3/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=365T; Drive=Direct | Open
412695 | GENERAL LINE | OK | cbc_qt_run_text | 344-22-455 quote run.txt |  |  | 412695 | 40 | A10 |  |  | 4S | 85.0 | TH | CW |  | 10000 | 10.00 | 100.0 | 1800 | 70 | 70 | 0.0750 | 100.0 | 1800 | 20466 | [8 empty] | 3.44 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011 CS | 0.179 ( 7) |  |  |  | 12 | 2391 | 3750 | 247 | 292 | 388 | 6.86 | 7.32 |  |  | 445T |  |  | 1785 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 9.165 |  | Not included |  |  | 3826 | 29187 | 19-5-16 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 3 3/8 | [11 empty] | Ambient Temp F=90 | Size=40; Design=A10; Arrangement=4S; % Width=85.0; Discharge=TH; Rotation=CW; CFM=10000; SP=10.00; BHP=100.0; RPM=1800; Max Temp F=70; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.179 ( 7); Hub=19-5-16; Blades=12; STH=3.44; Motor Frame=445T; Drive=Motor mounted | Open
412721 | HDX | OK | pdf_vision | QT RUN.pdf |  |  | SN#412721 | 3000 | 5500 |  |  | 9H1 | 100.0 | PCT | CW | 29 | 7000 | 16.35 | 22.3 | 2430 | 90 | 300 | 0.0520 | 30.0 | 2430 | 18449 | 1 11/16 | 12 | 4604 | 26 13/16 | 5.65 | 9 1/2 | 7 1/2 |  | 1.25 | 1 11/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 393 | FIXED | 105 | 76 | 60 | 3410 | 1045 STEEL | 0.51 | 0.62 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) |  |  | CARBON STEEL | 16 | 3870 | [6 empty] | 6.3 | 3.6 | 286T | W |  | 390 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 2.358 |  |  |  |  | 1927 | 45772 | 7/16 |  | Belt |  |  |  | Yes | Yes | [12 empty] | 41 | 12 7/8 | 7 |  | Yes | Ambient Temp F=90 | Size=3000; Design=5500; Arrangement=9H1; % Width=100.0; Discharge=PCT; Rotation=CW; CFM=7000; SP=16.35; BHP=22.3; RPM=2430; Max Temp F=300; Effective Wheel Dia=29; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.135 (10); Wheel Material=CARBON STEEL; Hub=7/16; Blades=16; Shaft Dia=1 11/16; Brg Centers=12; Critical Speed RPM=4604; BX=9 1/2; STB=7 1/2; OH=5.65; STH=1.25; Bearing Size=1 11/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=286T; Motor Position=W; Drive=Belt | Open
412737 | GENERAL LINE | OK | cbc_qt_run_text | 333-24-192 - QT Run Rev 1.txt |  |  | 412737 | 23 | 52 |  |  | 1S | 100.0 | TH | CW | 40 | 15898 | 8.00 | 34.9 | 1170 | 112 | 112 | 0.0610 | 40.0 | 1200 | 12566 | 1 15/16 | 27 | 1446 | 38 3/8 | 10.85 | 14 1/4 | 5 1/4 | 36 | 1.00 | 1 15/16 | LINK BELT SERIES 200 | 400000 | FIXED | -60 | FIXED | 323 | 105 | 198 | 1205 | 1045 STEEL | 0.54 | 0.39 |  |  | ASTM A1011 CS | 0.179 ( 7) |  |  | ASTM A1011 CS | 0.179 ( 7) |  |  |  | 6 | 1240 | 3600 | [21 empty] | FALK G20 | Direct |  |  |  |  | Yes | [5 empty] | 1 15/16 | [11 empty] | Ambient Temp F=70 | Size=23; Design=52; Arrangement=1S; % Width=100.0; Discharge=TH; Rotation=CW; CFM=15898; SP=8.00; BHP=34.9; RPM=1170; Max Temp F=112; Effective Wheel Dia=40; Blade Material=ASTM A1011 CS; Blade Gauge=0.179 ( 7); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.179 ( 7); Coupling=FALK G20; Blades=6; Shaft Dia=1 15/16; Brg Centers=27; Critical Speed RPM=1446; BX=14 1/4; STB=5 1/4; OH=10.85; STH=1.00; Bearing Size=1 15/16; Bearing Series=LINK BELT SERIES 200; Drive=Direct | Open
413044 | HDX | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | SN413044 | 2 | 1911 |  |  | 381 | 80.0 | TH | CW | 52 7/8 | 39590 | 10.00 | 89.0 | 1185 | 100 | 125 | 0.0690 | 125.0 | 1225 | 16957 | 3 15/16 | 76 13/16 | 1782 | 92.94 |  |  | 10.38 |  |  | 3/16 | DODGE PLAIN SLEEVEOLI BEARINGS |  | FIXED | 502 | FLOAT | 212 | 0 | 920 | 1426 |  | 0.18 | 0.85 |  |  | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A572 X-TEN | 1/4 |  |  | CAST STEEL | 8 | 1578 | [13 empty] | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 15.880 |  |  |  |  | 5248 | 204393 | 19-5-219 | THOMAS 71 SIZE 412 | Direct |  |  |  | Yes | [9 empty] | 2.1870 | 2.1860 | 2.1875 | 0.5000 X 0.2500 | 88 1/4 | 18 3/4 | 270 |  | Yes | Ambient Temp F=90 | Size=2; Design=1911; Arrangement=381; % Width=80.0; Discharge=TH; Rotation=CW; CFM=39590; SP=10.00; BHP=89.0; RPM=1185; Max Temp F=125; Effective Wheel Dia=52 7/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Wheel Material=CAST STEEL; Hub=19-5-219; Coupling=THOMAS 71 SIZE 412; Blades=8; Shaft Dia=3 15/16; Brg Centers=76 13/16; Critical Speed RPM=1782; STB=10.38; Bearing Size=3/16; Bearing Series=DODGE PLAIN SLEEVEOLI BEARINGS; Drive=Direct | Open
413224 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN CO#2.pdf |  |  | 413224 | 3612 | 5500 |  |  | 4S | 100.0 | UB | CW | 37 1/4 | 14400 | 16.80 | 50.1 | 1770 | 70 | 70 | 0.0739 | 60.0 | 1800 | 17554 | [8 empty] | 1.50 | [15 empty] | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 16 | 3222 |  | 154 | 109 | 169 | 2.83 | 3.70 |  |  | 364T |  |  | 835 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 3.477 |  | Not included |  | Included | 2386 | 49413 | 23-5-423 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 3/8 | [11 empty] | Ambient Temp F=70 | Size=3612; Design=5500; Arrangement=4S; % Width=100.0; Discharge=UB; Rotation=CW; CFM=14400; SP=16.80; BHP=50.1; RPM=1770; Max Temp F=70; Effective Wheel Dia=37 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=23-5-423; Blades=16; STH=1.50; Motor Frame=364T; Drive=Motor mounted | Open
413242 | GENERAL LINE | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | #413242 | 3612 | 6195 |  |  | 48 | 75.0 | DISCH TH | ROT CCW | 34 11/16 | 18000 | 10.00 | 37.2 | 1770 | 70 | 150 | 0.0750 | 50.0 | 1800 | 16340 | [8 empty] | 2.25 | [15 empty] | ASTM A240 304L SS | 3/16 | ASTM A240 304L SS | 3/16 | ASTM A240 304L SS | 3/8 |  |  | CAST 304 | 10 | 2154 | 6390 | 290 | 133 | 327 | 4.06 | 6.13 |  |  | 326T |  | ODP | 610 | 3/16 A240 304L SS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 6.566 |  | Not included |  | Yes | 2123 | 74099 | 19-5-1042 BORE 2 1/8 |  | Motor mounted | Required |  |  |  | Yes | [5 empty] | 2 1/8 | [11 empty] | Ambient Temp F=70; Wheel Weight=290; Thrust=133; Outlet=22 3/4 IN. X 41 9/16 IN.; Base=326T FR MOTOR; Motor Weight=610; Housing Material=3/16 A240 304L SS; Inlet Cone Ring Material=MILD STEEL; Stiffeners Material=A240 304 SS | Size=3612; Design=6195; Arrangement=48; % Width=75.0; Discharge=DISCH TH; Rotation=ROT CCW; CFM=18000; SP=10.00; BHP=37.2; RPM=1770; Max Temp F=150; Effective Wheel Dia=34 11/16; Blade Material=ASTM A240 304L SS; Blade Gauge=3/16; Sideplate Material=ASTM A240 304L SS; Sideplate Gauge=3/16; Backplate Material=ASTM A240 304L SS; Backplate Gauge=3/8; Wheel Material=CAST 304; Hub=19-5-1042 BORE 2 1/8; Blades=10; STH=2.25; Motor Frame=326T; Motor Enclosure=ODP; Drive=Motor mounted | Open
413260 | HDX | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 413260 | 5414 | 6100 |  |  | 8S | 100.0 | TH | CW |  | 101321 | 15.42 | 404.0 | 1780 | 95 | 95 | 0.0701 | 450.0 | 1800 | 25565 | 5 3/16 | 16 | 3203 | 47 1/2 | 18.33 | 29 11/16 | 11 5/8 |  | 3.38 | 5 3/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -905 | FLOAT | 2157 | 0 | 2484 | 1850 | 1045 STEEL | 0.20 | 0.15 |  |  | ASTM A6 XF-100 | 3/8 | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 1/2 |  |  |  | 10 | 2107 | 3050 | [10 empty] | 4343 | 3/8 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 15.920 |  | Included |  | Included | 12729 | 175961 | 19-5-12 | FALK T10 | Direct | Required | Required | Yes | Yes | [6 empty] | 4 15/16 |  |  | 3.4370 | 3.4355 | 3.4375 | 0.8750 X 0.4375 |  |  |  | SK-19-72 | Yes | Ambient Temp F=70 | Size=5414; Design=6100; Arrangement=8S; % Width=100.0; Discharge=TH; Rotation=CW; CFM=101321; SP=15.42; BHP=404.0; RPM=1780; Max Temp F=95; Blade Material=ASTM A6 XF-100; Blade Gauge=3/8; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Hub=19-5-12; Coupling=FALK T10; Blades=10; Shaft Dia=5 3/16; Brg Centers=16; Critical Speed RPM=3203; BX=29 11/16; STB=11 5/8; OH=18.33; STH=3.38; Bearing Size=5 3/16; Bearing Series=LINK BELT SERIES 6800; Drive=Direct | Open
413265 | GENERAL LINE | CHECK VISION | pdf_vision | qt run.pdf |  |  | SN#413265 | 3612 | 6105 |  |  | 88 | 100.0 | CCW | CCW | 38 5/16 | 25169 | 15.07 | 73.6 | 1780 | 95 | 95 | 0.0701 | 100.0 | 1800 | 18060 | 2 15/16 | 12 | 4470 | 31 3/4 | 9.13 | 16 1/2 | 8 1/4 | 61 | 2.25 | 2 15/16 | 6800 | 400000 | FIXED | -189 | FLOAT | 591 | 0 | 392 | 2972 | 1045 STEEL | 0.22 | 0.18 |  |  | ASTM A6 XF-100 | 1/4 | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 3/8 |  |  | CAST IRON | 10 |  | 4630 | [7 empty] | 405T |  |  | 1575 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 7.216 |  |  |  | Included | 3922 | 75285 | BORE 2 15/16 | FALK T10, SIZE 1080T, BORE 2.938 | Direct | Required |  | Yes |  | Yes | [5 empty] | 2 15/16 |  |  | 2.9370 | 2.9355 | 2.9375 | 0.7500 X 0.3750 |  |  |  |  | Yes | Ambient Temp F=70 | Size=3612; Design=6105; Arrangement=88; % Width=100.0; Discharge=CCW; Rotation=CCW; CFM=25169; SP=15.07; BHP=73.6; RPM=1780; Max Temp F=95; Effective Wheel Dia=38 5/16; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Wheel Material=CAST IRON; Hub=BORE 2 15/16; Coupling=FALK T10, SIZE 1080T, BORE 2.938; Blades=10; Shaft Dia=2 15/16; Brg Centers=12; Critical Speed RPM=4470; BX=16 1/2; STB=8 1/4; OH=9.13; STH=2.25; Bearing Size=2 15/16; Bearing Series=6800; Motor Frame=405T; Drive=Direct | Open
413412 | HDX | OK | pdf_vision | QT RUN.pdf |  |  | SN413412 | 2800 | 2310B |  |  | 8S | 65.0 | UB | CCW | 30 13/16 | 7300 | 70.0 | 118.3 | 3550 | 70 | 100 | 0.0750 | 125.0 | 3600 | 29028 | 1 15/16 | 10 | 5946 | 3 3/4 | 6.09 | 6 9/16 | 6 |  | 1.55 | 1 15/16 | 6800 | 122217 | FIXED | -25 | FLOAT | 161 | 0 | 66 | 4020 |  | 0.62 | 0.40 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) |  |  | CAST STEEL | 11 | 4020 | 10450 | [7 empty] | 444TS | [12 empty] | 23-5-423 | FALK G20, SIZE 1020G, BORE 1.938 | Direct | Required | Required |  | Yes | Yes | [5 empty] | 1 11/16 |  |  | 1.9370 | 1.9360 | 1.9375 | .0.5000 X 0.2500 | [5 empty] | Ambient Temp F=90 | Size=2800; Design=2310B; Arrangement=8S; % Width=65.0; Discharge=UB; Rotation=CCW; CFM=7300; SP=70.0; BHP=118.3; RPM=3550; Max Temp F=100; Effective Wheel Dia=30 13/16; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.135 (10); Wheel Material=CAST STEEL; Hub=23-5-423; Coupling=FALK G20, SIZE 1020G, BORE 1.938; Blades=11; Shaft Dia=1 15/16; Brg Centers=10; Critical Speed RPM=5946; BX=6 9/16; STB=6; OH=6.09; STH=1.55; Bearing Size=1 15/16; Bearing Series=6800; Motor Frame=444TS; Drive=Direct | Open
413419 | HDX | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 413419 | 3300 | 1903 |  |  | 4S | 95.0 | UB | CW | 34 5/8 | 30552 | 55.00 | 320.2 | 3571 | 70 | 100 | 0.0735 | 350.0 | 3600 | 32657 | 2 15/16 | 12 | 4647 | 29 1/4 | 8.45 | 14 11/16 | 7 1/4 | 56 | 2.12 | 2 15/16 | LINK BELT SERIES 300 | 400000 | FIXED | -173 | FIXED | 609 | 173 | 356 | 3600 | 1045 STEEL | 0.35 | 0.32 |  |  | ASTM A6 XF-100 | 3/16 | ASTM A6 XF-100 | 5/16 | ASTM A572 X-TEN | 3/8 |  |  |  | 10 | 4055 | 5070 | 346 | 173 | 355 | 4.95 | 6.01 |  |  | 449TS |  |  | 2600 | 3/8 C.Q. HRS | SK-9-236 HI PRESSURE, 18 IN. CENTERS | 5.837 |  | Not included |  | Included | 5334 | 80240 | 19-5-11 | FALK G20 | Motor mounted |  | Required | Yes | [7 empty] | 2 3/8 |  |  | 2.9370 | 2.9355 | 2.9375 | 0.7500 X 0.3750 |  |  |  | SK-19-72 | Yes | Ambient Temp F=70 | Size=3300; Design=1903; Arrangement=4S; % Width=95.0; Discharge=UB; Rotation=CW; CFM=30552; SP=55.00; BHP=320.2; RPM=3571; Max Temp F=100; Effective Wheel Dia=34 5/8; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=5/16; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Hub=19-5-11; Coupling=FALK G20; Blades=10; Shaft Dia=2 15/16; Brg Centers=12; Critical Speed RPM=4647; BX=14 11/16; STB=7 1/4; OH=8.45; STH=2.12; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=449TS; Drive=Motor mounted | Open
413554 | HD-PFD-IAF | OK | cbc_qt_run_text | QUOTE RUN.txt |  |  | 413554 | 4412 | 1904 |  | PACKAGED FORCED DRAFT FAN | 4S1 | 75.0 | DB | CCW | 48 15/16 | 33495 | 23.47 | 156.6 | 1770 | 100 | 125 | 0.0631 | 200.0 | 1800 | 23067 | [8 empty] | 2.81 | [15 empty] | ASTM A1011-HSLAS | 0.060 (16) | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM CQ HRS A36 | 3/8 |  |  |  | 10 | 2109 | 2640 | 455 | 436 | 869 | 4.93 | 7.19 |  |  | 447T |  | TEFC | 2850 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 9.844 |  | Not included |  |  |  |  | 19-5-289 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 3 3/8 | [6 empty] | 80 | 17 | 1 |  |  | Ambient Temp F=90 | Size=4412; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S1; % Width=75.0; Discharge=DB; Rotation=CCW; CFM=33495; SP=23.47; BHP=156.6; RPM=1770; Max Temp F=125; Effective Wheel Dia=48 15/16; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 ( 7); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=3/8; Hub=19-5-289; Blades=10; STH=2.81; Motor Frame=447T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
413592 | HDX | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | SN413592 | 3200 | 2300B |  |  | 18 | 100.0 | UB | CW | 32 | 6106 | 20.00 | 29.1 | 2464 | 365 | 365 | 0.0410 | 100.0 | 2894 | 24245 | 2 11/16 | 20 | 4069 | 42 1/2 | 10.66 | 11 1/2 | 11 1/8 | 1.5 |  | 2 11/16 | 6800 | 400000 | FLOAT | 500 | FIXED | 146 | 89 | 88 | 3200 | 1045 STEEL | 0.31 | 0.66 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) |  |  | CAST STEEL | 11 | 3530 | 4760 | [5 empty] | 6.2 | 3.4 |  |  |  |  | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 19 IN. CENTERS | 1.025 |  |  |  |  | 1303 | 44873 | HUB 23-3-423 BORE 2 7/16 |  | Belt |  |  |  | Yes | Yes | [5 empty] | 2 7/16 | [10 empty] | Yes | Ambient Temp F=90 F | Size=3200; Design=2300B; Arrangement=18; % Width=100.0; Discharge=UB; Rotation=CW; CFM=6106; SP=20.00; BHP=29.1; RPM=2464; Max Temp F=365; Effective Wheel Dia=32; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.135 (10); Wheel Material=CAST STEEL; Hub=HUB 23-3-423 BORE 2 7/16; Blades=11; Shaft Dia=2 11/16; Brg Centers=20; Critical Speed RPM=4069; BX=11 1/2; STB=11 1/8; OH=10.66; Bearing Size=2 11/16; Bearing Series=6800; Drive=Belt | Open
413596 | HDX | OK | cbc_qt_run_text | QT RUN-CO#1.pdf |  |  | 413596 | 6600 | 1910 |  |  | 7S1 | 75.0 | TAU | CCW |  | 109046 | 37.45 | 777.3 | 1480 | 105 | 125 | 0.0690 | 800.0 | 1500 | 27966 | 6 3/4 | 99 | 2208 |  |  |  | 11.50 |  | 4.94 | 3 15/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 1850 | FIXED | 776 | 549 | 5782 | 1576 | 1045 STEEL | 0.17 | 0.75 |  |  | ASTM A1011-HSLAS | 0.105 (12) | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/2 |  |  |  | 12 | 1675 | 2380 | [7 empty] | 10 |  | ODP | 8123 | 3/8 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 23.964 | 73.000 |  |  |  | 35965 | 401333 | 19-5-1434 | FALK T10 | Direct |  | Required |  | Yes | [9 empty] | 3.9370 | 3.9355 |  | 1.0000 X 0.5000 | 131 1/2 | 27 7/8 | 1613 | SK-19-72 | Yes | Ambient Temp F=90 | Size=6600; Design=1910; Arrangement=7S1; % Width=75.0; Discharge=TAU; Rotation=CCW; CFM=109046; SP=37.45; BHP=777.3; RPM=1480; Max Temp F=125; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Hub=19-5-1434; Coupling=FALK T10; Blades=12; Shaft Dia=6 3/4; Brg Centers=99; Critical Speed RPM=2208; STB=11.50; STH=4.94; Bearing Size=3 15/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=10; Motor Enclosure=ODP; Drive=Direct | Open
413596 | HDX | UNRECOGNIZED FORMAT | unknown | OUTLET DAMPER QT RUN.doc | DAMPER | [104 empty] | Open
413596 | HDX | UNRECOGNIZED FORMAT | unknown | PRE-SPIN INLET DAMPER QT RUN-13 BLADES.doc | DAMPER | [104 empty] | Open
413651 | HDX | OK | pdf_vision | QT RUN.pdf |  |  | SN#413651 | 4412 | 6100 |  |  | 8S1 | 85.0 | 270 | CW |  | 35877 | 17.02 | 122.6 | 1770 | 150 | 180 | 0.0616 | 150.0 | 1800 | 20970 | 3 3/16 | 14 | 3492 | 34 | 10.47 | 18 15/16 | 7 7/8 | MI.5 76 | 2.81 | 3 3/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -297 | FLOAT | 891 | 0 | 882 | 1939 | 4140 STEEL | 0.39 | 0.24 |  |  | ASTM A6 XF-100 | 3/8 | ASTM A6 XF-100 | 1/4 | ASTM A6 XF-100 | 5/16 |  |  | CAST IRON | 10 | 2070 | 3730 | [7 empty] | 445T |  |  | 1785 | 1/4 A572 X-TEN | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 10.195 |  |  |  |  | 7277 | 191541 | 2.9375 | THOMAS 71 SIZE 375 BORE 3.188 | Direct |  |  | Yes | Yes | Yes | [5 empty] | 2 15/16 |  |  | 3.1870 | 3.1855 | 3.1875 | 0.7500 x 0.3750 | 80 | 17 | 270 |  | Yes | Ambient Temp F=150.0 | Size=4412; Design=6100; Arrangement=8S1; % Width=85.0; Discharge=270; Rotation=CW; CFM=35877; SP=17.02; BHP=122.6; RPM=1770; Max Temp F=180; Blade Material=ASTM A6 XF-100; Blade Gauge=3/8; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=1/4; Backplate Material=ASTM A6 XF-100; Backplate Gauge=5/16; Wheel Material=CAST IRON; Hub=2.9375; Coupling=THOMAS 71 SIZE 375 BORE 3.188; Blades=10; Shaft Dia=3 3/16; Brg Centers=14; Critical Speed RPM=3492; BX=18 15/16; STB=7 7/8; OH=10.47; STH=2.81; Bearing Size=3 3/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=445T; Drive=Direct | Open
413680 | HDX | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | S/N 4110650 | 3000 | 5800 |  |  | 4S | 100.0 | BH | CW | 30 | 54.00 BH | 87.7 BHP | 150.0 | 3500 | 70 | 70 | 0.0750 | 150.0 | 3600 | 28274 | POWER SHAFT DIAMETER SPECIFIED - ENGINEERING APPROVAL REQUIRED | 1.38 | [22 empty] | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) |  |  | 10 BLADES | 10 | 4255 |  | 99 | 156 | 63 | 2.45 | 3.62 IN. |  |  | 445TS |  | TEFC | 1937 | 1/4 C.Q. HRS |  | 1.172 |  | Not included |  | INCLUDED | 3372 | 43707 | HUB 23-5-423 BORE 2 3/8 CAST STEEL |  | Motor mounted | Required |  |  |  | Yes | [5 empty] | 2 3/8 | [11 empty] | Ambient Temp F=90 F; Wheel Weight=99 LB; Thrust=156 LB; WR2=63 LB-FT2; Outlet N X A=12 IN. X 14 1/16 IN.; Base=445TS FR MOTOR; Motor Mounting=INCLUDED; Motor Weight=1937; Diffuser=SK 9-236 HI PRESSURE, 18 IN. CENTERS; Split Housing=1/4 C.Q. HRS; Outlet Damper Torque=315 IN-LB AT PEAK SP STD AIR; Damper Frame=OF A36; Damper Frame Thickness=1/4 PER SKE-449; Manual Control=WITH OPERATING HANDLE LOC. 1, POS. 270 | Size=3000; Design=5800; Arrangement=4S; % Width=100.0; Discharge=BH; Rotation=CW; CFM=54.00 BH; SP=87.7 BHP; BHP=150.0; RPM=3500; Max Temp F=70; Effective Wheel Dia=30; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.135 (10); Wheel Material=10 BLADES; Hub=HUB 23-5-423 BORE 2 3/8 CAST STEEL; Blades=10; Shaft Dia=POWER SHAFT DIAMETER SPECIFIED - ENGINEERING APPROVAL REQUIRED; Brg Centers=1.38; Motor Frame=445TS; Motor Enclosure=TEFC; Drive=Motor mounted | Open
413810 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN-2.9375 Shaft.txt |  |  | 413810 | 3300 | 6195 |  |  | 9H | 100.0 | TH | CW | 31 3/8 | 24000 | 26.50 | 123.8 | 2822 | 70 | 70 | 0.0731 | 125.0 | 2822 | 23161 | 2 15/16 | 12 | 5130 | 34 1/2 | 8.64 | 15 3/8 | 12 | 66 | 2.12 | 2 15/16 | LINK BELT SERIES 6800 | 108263 | FLOAT | 2483 | FIXED | 770 | 219 | 267 | 3000 | 1045 STEEL | 0.17 | 0.58 | 22 3/4 | 23 7/8 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM CQ HRS A36 | 3/8 |  |  |  | 10 | 3137 | 6130 | [5 empty] | 5.4 | 4.0 | 444T | Z |  | 1515 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 5.934 |  | Included |  | Included | 3236 | 42294 | 19-5-16 |  | Belt | Required |  | Yes |  | Yes | [5 empty] | 2 15/16 | [10 empty] | Yes | Ambient Temp F=70; Discharge Height (A)=37 9/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=26 1/8; Unitary Base To Cl (LB)=75 3/8; Motor Cl To Fan Cl (LM)=53 1/4; Shaft Height (H)=30 1/16; Total Vert Height (TV)=69 5/8; Max Right of CL to Hsg (RH)=26 1/8; Max Left of CL to Disch (LH)=32 9/16; Mounting Channel (MA)=2 1/2; Base Flange to CL (D)=32 1/8; Drive End of Shaft to CL (K)=39 3/8; Mtg Flange to CL (LR)=13 7/8 | Size=3300; Design=6195; Arrangement=9H; % Width=100.0; Discharge=TH; Rotation=CW; CFM=24000; SP=26.50; BHP=123.8; RPM=2822; Max Temp F=70; Effective Wheel Dia=31 3/8; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM CQ HRS A36; Backplate Gauge=3/8; Hub=19-5-16; Blades=10; Shaft Dia=2 15/16; Brg Centers=12; Critical Speed RPM=5130; BX=15 3/8; STB=12; OH=8.64; STH=2.12; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=22 3/4; Base to CL (F)=23 7/8; Motor Frame=444T; Motor Position=Z; Drive=Belt | Open
413952 | GENERAL LINE | OK | pdf_vision | 413952 QT RUN.pdf |  |  | 413952 | 40 | B10 |  |  | 8S | 85.0 | UB | CCW | 41.4 | 35851 | 1.00 | 41.4 | 1170 | 120 | 120 | 0.0656 | 50.0 | 1200 | 13644 | 2 15/16 | 23 1/4 | 2693 | 46 13/16 | 13.25 | 23 | 8 1/2 | 90 | 3.44 | 2 15/16 | LINK BELT SERIES 200 | 400000 | FIXED | -64 | FIXED | 390 | 135 | 366 | 1344 | 1045 STEEL | 0.19 | 0.14 |  |  | ASTM A1011-HSLAS | 0.179 (7) | ASTM A1011 CS | 0.105 (12) | ASTM A1011 CS | 0.179 (7) |  |  | RES 1690 CPM | 8 | 1344 | 1690 | [7 empty] | 365T |  |  | 920 |  | SK-9-236 MED PRESSURE, 30 IN. CENTERS | 9.199 |  |  |  | Included |  |  | HUB 4-5-121 BORE 2 15/16 FAB. STL. | FAIK T10, SIZE 1080T, BORE 2.938 NOT INCL. | Direct |  |  |  |  | Yes | [16 empty] | Yes | Ambient Temp F=120 | Size=40; Design=B10; Arrangement=8S; % Width=85.0; Discharge=UB; Rotation=CCW; CFM=35851; SP=1.00; BHP=41.4; RPM=1170; Max Temp F=120; Effective Wheel Dia=41.4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 (7); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.179 (7); Wheel Material=RES 1690 CPM; Hub=HUB 4-5-121 BORE 2 15/16 FAB. STL.; Coupling=FAIK T10, SIZE 1080T, BORE 2.938 NOT INCL.; Blades=8; Shaft Dia=2 15/16; Brg Centers=23 1/4; Critical Speed RPM=2693; BX=23; STB=8 1/2; OH=13.25; STH=3.44; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 200; Motor Frame=365T; Drive=Direct | Open
413967 | GENERAL LINE | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | 413967 | 7300 | 6195 |  |  | 851 | 80.0 | 0 | CCW | 69 3/8 | 145.8 | 1182 | 0.90 | 700 | 90 | 800 | 0.0330 | 150.0 | 1200 | 21787 | 5 15/16 | 24 | 2166 | 62 1/2 | 23.63 | 3/16 | 12 | 5/8 | 3.88 | 5 15/16 | LINK-BELT SERIES 6800 | 400000 | FIXED | -1064 | FLOAT | 2877 | 0 | 5960 | 1300 | 1045 STEEL | 0.26 | 0.06 |  |  | ASTM A6 XP-100 | 3/16 | ASTM A6 XP-100 | 5/16 | ASTM A6 XP-100 | 3/8 |  |  | CAST-STEEL | 10 | 1335 | 1670 | [7 empty] | 447T |  |  | 2280 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 26.874 |  |  |  |  | 19373 | 296584 | BORE 5 11/16 | FALK T10, SIZE 1100T, BORE 3.438 | Direct | Required |  | Yes | Yes | Yes | [5 empty] | 5 11/16 |  |  | 3.4370 | 3.4355 | 3.4375 |  | 131 1/2 | 27 7/8 | 1613 |  | Yes | Ambient Temp F=90 | Size=7300; Design=6195; Arrangement=851; % Width=80.0; Discharge=0; Rotation=CCW; CFM=145.8; SP=1182; BHP=0.90; RPM=700; Max Temp F=800; Effective Wheel Dia=69 3/8; Blade Material=ASTM A6 XP-100; Blade Gauge=3/16; Sideplate Material=ASTM A6 XP-100; Sideplate Gauge=5/16; Backplate Material=ASTM A6 XP-100; Backplate Gauge=3/8; Wheel Material=CAST-STEEL; Hub=BORE 5 11/16; Coupling=FALK T10, SIZE 1100T, BORE 3.438; Blades=10; Shaft Dia=5 15/16; Brg Centers=24; Critical Speed RPM=2166; BX=3/16; STB=12; OH=23.63; STH=3.88; Bearing Size=5 15/16; Bearing Series=LINK-BELT SERIES 6800; Motor Frame=447T; Drive=Direct | Open
413968 | GENERAL LINE | OK | d64_wheel_construction | 311-23-2067 D64 Wheel Construction (Inner Ring).xlsx | [103 empty] | Fan Size=222; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=25000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.3125 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=222; Outer Ring Thickness=0.3125; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=25000 | Open
414049 | HD-PFD-IAF | OK | cbc_qt_run_text | 414049_348-24-1023 - QT Run.txt |  |  | 414049 | 2000 | 1903 |  | PACKAGED FORCED DRAFT FAN | 4S | 85.0 | UB | CCW | 21 | 5288 | 24.10 | 25.5 | 3500 | 15 | 70 | 0.0921 | 30.0 | 3600 | 19792 | [8 empty] | 1.25 | [15 empty] | ASTM A1011-HSLAS | 0.048 (18) | ASTM A1011-HSLAS | 0.048 (18) | ASTM A1011-HSLAS | 0.135 (10) |  |  |  | 10 | 4125 | 5690 | 45 | 62 | 13 | 2.17 | 4.25 |  |  | 284T |  | ODP | 355 | 10 GA A607 X-TEN | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 2.059 |  | Not included |  | Yes |  |  | 19-5-1055 |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q1 BUSHING 1 7/8 | [10 empty] | Size=2000; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S; % Width=85.0; Discharge=UB; Rotation=CCW; CFM=5288; SP=24.10; BHP=25.5; RPM=3500; Max Temp F=70; Effective Wheel Dia=21; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.048 (18); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.048 (18); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.135 (10); Hub=19-5-1055; Blades=10; STH=1.25; Motor Frame=284T; Motor Enclosure=ODP; Drive=Motor mounted | Open
414183 | GENERAL LINE | OK | d64_wheel_construction | 414183_D64 Wheel Construction (Outer Ring) 345-20-1754.xlsx | [103 empty] | Fan Size=182; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=50000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.25 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=182; Outer Ring Thickness=0.25; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=50000 | Open
414185 | GENERAL LINE | OK | d64_wheel_construction | 414185_333-18-2686 D64 Wheel Construction (Outer Ring).xlsx | [103 empty] | Fan Size=150; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=50000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.1345 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=150; Outer Ring Thickness=0.1345; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=50000 | Open
414186 | GENERAL LINE | OK | d64_wheel_construction | 414186_333-18-2686 D64 Wheel Construction (Outer Ring).xlsx | [103 empty] | Fan Size=150; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=50000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.1345 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=150; Outer Ring Thickness=0.1345; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=50000 | Open
414193 | HDX | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 414193 | 5414 | 5800 |  |  | 8S | 100.0 | BAU | CCW | 58 | 29000 | 47.00 | 279.5 | 1780 | 113 | 113 | 0.0693 | 300.0 | 1800 | 27332 | 2 15/16 | 16 | 3927 | 35 9/16 | 7.98 | 14 7/8 | 8 3/4 | 68 | 2.50 | 2 15/16 | LINK BELT SERIES 6800 | 306980 | FIXED | -164 | FLOAT | 735 | 0 | 1263 | 2170 | 1045 STEEL | 0.58 | 0.55 |  |  | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A572 X-TEN | 5/16 |  |  |  | 10 | 2170 | [8 empty] | 449T |  | ODP | 2840 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 19 IN. CENTERS | 3.842 |  | Included |  | Included | 8101 | 108273 | 49-5-145- | FALK T10 | Direct |  | Required | [8 empty] | 2 15/16 |  |  | 2.9370 | 2.9355 | 2.9375 | 0.7500 X 0.3750 |  |  |  |  | Yes | Ambient Temp F=70 | Size=5414; Design=5800; Arrangement=8S; % Width=100.0; Discharge=BAU; Rotation=CCW; CFM=29000; SP=47.00; BHP=279.5; RPM=1780; Max Temp F=113; Effective Wheel Dia=58; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=49-5-145-; Coupling=FALK T10; Blades=10; Shaft Dia=2 15/16; Brg Centers=16; Critical Speed RPM=3927; BX=14 7/8; STB=8 3/4; OH=7.98; STH=2.50; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=449T; Motor Enclosure=ODP; Drive=Direct | Open
414206 | GENERAL LINE | OK | cbc_qt_run_text | 414206 QT RUN.docx |  |  | 414206 | 24 | B10 | 4 |  | 9H | 100.0 | UB | CW |  | 17000 | 10.00 | 42.3 | 2649 | 170 | 300 | 0.0540 | 50.0 | 2649 | 18333 | 2 7/16 | 12 | 3449 | 35 7/16 | 12.16 | 17 7/16 | 9 15/16 |  | 2.50 | 2 7/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 777 | FIXED | 212 | 90 | 71 | 2759 | A240 304 SS | 0.25 | 0.61 |  |  | ASTM A240 304L SS | 0.135 (10) | ASTM A240 304L SS | 3/16 | ASTM A240 304L SS | 3/16 |  |  |  | 12 | 2787 | 4420 | [5 empty] | 5.8 | 3.3 | 326T | W |  | 610 | 10 GA A240 304L SS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 3.574 | [6 empty] | 4-5-145 |  | Belt |  |  | Yes |  | Yes | [5 empty] | 2 7/16 | [10 empty] | Yes | Ambient Temp F=70 | Size=24; Design=B10; Arrangement=9H; % Width=100.0; Discharge=UB; Rotation=CW; Class=4; CFM=17000; SP=10.00; BHP=42.3; RPM=2649; Max Temp F=300; Blade Material=ASTM A240 304L SS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A240 304L SS; Sideplate Gauge=3/16; Backplate Material=ASTM A240 304L SS; Backplate Gauge=3/16; Hub=4-5-145; Blades=12; Shaft Dia=2 7/16; Brg Centers=12; Critical Speed RPM=3449; BX=17 7/16; STB=9 15/16; OH=12.16; STH=2.50; Bearing Size=2 7/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=326T; Motor Position=W; Drive=Belt | Open
414308 | GENERAL LINE | OK | cbc_qt_run_text | quote run, wheel 1800.txt |  |  | 414308 | 22 | A10 |  |  | 4S | 100.0 | BAU | CW |  | 10000 | 10.00 | 20.0 | 1800 | 70 | 70 | 0.0750 | 20.0 | 1800 | 11313 | [8 empty] | 2.27 | [15 empty] | ASTM A1008 HSLAS | 0.048 (18) | ASTM A1011 CS | 0.060 (16) | ASTM A1011 CS | 0.105 (12) |  |  |  | 12 | 2848 | 6870 | 53 | 27 | 23 | 4.38 | 5.90 |  |  | 256T |  | ODP | 250 | 10 GA C.Q. HRS | SK-9-236 LOW PRESSURE, 36 IN. CENTERS | 2.945 |  | Not included |  |  |  |  | 4-5-14 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 1 5/8 | [11 empty] | Ambient Temp F=90 | Size=22; Design=A10; Arrangement=4S; % Width=100.0; Discharge=BAU; Rotation=CW; CFM=10000; SP=10.00; BHP=20.0; RPM=1800; Max Temp F=70; Blade Material=ASTM A1008 HSLAS; Blade Gauge=0.048 (18); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.060 (16); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.105 (12); Hub=4-5-14; Blades=12; STH=2.27; Motor Frame=256T; Motor Enclosure=ODP; Drive=Motor mounted | Open
414470 | HD-PFD-IAF | OK | cbc_qt_run_text | quote run 4-20.txt |  |  | 414470 | 3000 | 1902 |  |  | 4S | 75.0 | TAU | CW |  | 7586 | 9.38 | 13.5 | 1776 | 40 | 129 | 0.0680 | 20.0 | 1800 | 14137 | [8 empty] | 1.94 | [15 empty] | ASTM A240 316L SS | 0.060 (16) | ASTM A240 316L SS | 0.105 (12) | ASTM A240 316L SS | 1/4 |  |  |  | 10 | 1886 | 2360 | 130 | 68 | 97 | 3.27 | 4.19 |  |  | 286T |  | TEFC | 487 | 10 GA C.Q. HRS | SK-9-236 MED PRESSURE, 30 IN. CENTERS | 4.443 |  | Not included |  | Yes | 1310 | 32165 | 19-5- |  | Motor mounted |  |  | Yes |  | Yes | [5 empty] | 1 7/8 | [11 empty] | Ambient Temp F=70 | Size=3000; Design=1902; Arrangement=4S; % Width=75.0; Discharge=TAU; Rotation=CW; CFM=7586; SP=9.38; BHP=13.5; RPM=1776; Max Temp F=129; Blade Material=ASTM A240 316L SS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A240 316L SS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A240 316L SS; Backplate Gauge=1/4; Hub=19-5-; Blades=10; STH=1.94; Motor Frame=286T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
414648 | HD-PFD-IAF | CHECK VISION | pdf_vision | QT RUN REV A.pdf |  |  | SN414648 | 3300 | 1903 |  | PACKAGED FORCED DRAFT FAN | 98 | 100.0 | PCT,DISCH UB | NOT CW | 34 5/8 | 20000 | 8.00 | 37.9 | 1760 | 70 | 70 | 0.0733 | 40.0 | 1800 | 16328 | 1 15/16 | 12 | 3454 | 26 1/16 | 7.71 | 14 7/16 | 6 1/8 | 22 | 2.12 | 1 15/16 | LINK BELT SERIES 300 | 400000 | FIXED | -75 | FIXED | 255 | 43 | 150 | 2119 | 1045 STEEL | 0.32 | 0.25 |  |  | ASTM A1011-HSLAS | 0.060 (16) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 (7) |  |  |  | 10 | 2119 | 2650 | [7 empty] | 324T |  |  |  | 7 GA C.Q. HRS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 5.934 |  |  |  | Included |  |  | HUB 19-5-1057, Q1 BUSHING 1 15/16, C. IRON | FALK T10, SIZE 1060T, BORE 1.938 NOT INCL. | Direct |  |  |  |  | Yes | [7 empty] | Q1 BUSHING 1 15/16 | [8 empty] | Yes | Ambient Temp F=90; Manufacturer=GALLAGHER-KAISER; Coupling Ref=SKE-9-356 | Size=3300; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=98; % Width=100.0; Discharge=PCT,DISCH UB; Rotation=NOT CW; CFM=20000; SP=8.00; BHP=37.9; RPM=1760; Max Temp F=70; Effective Wheel Dia=34 5/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 (7); Hub=HUB 19-5-1057, Q1 BUSHING 1 15/16, C. IRON; Coupling=FALK T10, SIZE 1060T, BORE 1.938 NOT INCL.; Blades=10; Shaft Dia=1 15/16; Brg Centers=12; Critical Speed RPM=3454; BX=14 7/16; STB=6 1/8; OH=7.71; STH=2.12; Bearing Size=1 15/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=324T; Drive=Direct | Open
414651 | HD-PFD-IAF | CHECK VISION | pdf_vision | QT RUN REV A.pdf |  |  | SN414651 | 4014 | 1903 |  | PACKAGED FORCED DRAFT FAN | 88 | 100.0 | PCT, DISCH UB, ROT CW | CW | 42 1/4 | 40000 | 12.00 | 117.4 | 1760 | 70 | 70 | 0.0733 | 125.0 | 1800 | 19916 | 2 7/16 | 14 | 3489 | 32 9/16 | 8.39 | 17 1/8 | 8 7/16 | 43 | 2.50 | 2 7/16 | LINK BRITT SERIES 300 | 400000 | FIXED | -96 | FIXED | 434 | 96 | 378 | 2088 | 1045 STEEL | 0.44 | 0.39 |  |  | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.075 (14) | ASTM CQ HRS A36 | 1/4 |  |  | BORE 2 7/16 CAST IRON | 10 | 2088 | 2610 | [7 empty] | 444T |  | TEFC | 1893 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 8.828 |  |  |  | Included |  |  | HUB 19-5-16 | FALK T10, SIZE 1090T, BORE 2.438 NOT INCL. | Direct |  |  |  |  | Yes | [5 empty] | 2 7/16 | [10 empty] | Yes | Ambient Temp F=90 | Size=4014; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=88; % Width=100.0; Discharge=PCT, DISCH UB, ROT CW; Rotation=CW; CFM=40000; SP=12.00; BHP=117.4; RPM=1760; Max Temp F=70; Effective Wheel Dia=42 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.075 (14); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Wheel Material=BORE 2 7/16 CAST IRON; Hub=HUB 19-5-16; Coupling=FALK T10, SIZE 1090T, BORE 2.438 NOT INCL.; Blades=10; Shaft Dia=2 7/16; Brg Centers=14; Critical Speed RPM=3489; BX=17 1/8; STB=8 7/16; OH=8.39; STH=2.50; Bearing Size=2 7/16; Bearing Series=LINK BRITT SERIES 300; Motor Frame=444T; Motor Enclosure=TEFC; Drive=Direct | Open
414657 | HD-PFD-IAF | OK | pdf_vision | QT RUN REV A.pdf |  |  | SN414657 | 3300 | 1903 | ARR 8S | PACKAGED FORCED DRAFT FAN | 8S | 75.0 | DISCH BAU, ROT CW | CW | 34 5/8 | 13950 | 10.00 | 29.9 | 1770 | 70 | 70 | 0.0733 | 40.0 | 1800 | 16328 | 1 15/16 | 12 | 3956 | 26 1/16, OH 7.04, BX 13 7/16, STB 6 1/8 | 7.04 | 13 7/16 | 6 1/8 | 22 | 2.12 | 1 15/16 | LINK BELT SERIES 300 | 400000 | FIXED | -61 | FIXED | 233 | 43 | 138 LB-FT2 | 2202 | 1045 STEEL | 0.30 | 0.25 |  |  | ASTM A1011-HSLAS | 0.060 (16) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 (7) |  |  |  | 10 | 2202 | 2750 | [7 empty] | 324T |  | TEFC | 687 | 7 GA C.Q. HRS | SK-9-236 MED PRESSURE, 24 IN. CENTERS |  |  |  |  | Included |  |  | HUB 19-5-1057, Q1 BUSHING 1 15/16, C. IRON | FALK T10, SIZE 1060T, BORE 1.938 | Direct |  |  |  |  | Yes | [7 empty] | Q1 BUSHING 1 15/16 | [8 empty] | Yes | Ambient Temp F=90 F; Manufacturer=CHICAGO BLOWER CORP.; Company=GALLAGHER-KAISER; Wheel=10 BLADES, RES 2750 CPM | Size=3300; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=8S; % Width=75.0; Discharge=DISCH BAU, ROT CW; Rotation=CW; Class=ARR 8S; CFM=13950; SP=10.00; BHP=29.9; RPM=1770; Max Temp F=70; Effective Wheel Dia=34 5/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 (7); Hub=HUB 19-5-1057, Q1 BUSHING 1 15/16, C. IRON; Coupling=FALK T10, SIZE 1060T, BORE 1.938; Blades=10; Shaft Dia=1 15/16; Brg Centers=12; Critical Speed RPM=3956; BX=13 7/16; STB=6 1/8; OH=7.04; STH=2.12; Bearing Size=1 15/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=324T; Motor Enclosure=TEFC; Drive=Direct | Open
414667 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 414667 | 3000 | 5800 |  |  | 8S | 100.0 | BH | CCW | 32 1/2 | 4562 | 6.15 | 7.1 | 1770 | 500 | 650 | 0.0347 | 15.0 | 1800 | 15315 | 1 15/16 | 12 | 3591 | 27 13/16 | 8.06 | 11 9/16 | 6 1/8 | 23 | 1.38 | 1 15/16 | LINK BELT SERIES 300 | 400000 | FIXED | -54 | FIXED | 198 | 46 | 84 | 2872 | 1045 STEEL | 0.24 | 0.11 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) |  |  |  | 10 | 3709 | [8 empty] | 254T |  |  | 230 | 10 GA C.Q. HRS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 1.172 |  | Included |  | Included | 1241 | 43971 | 23-5-423 | FALK T10 | Direct |  |  |  |  | Yes | [5 empty] | 1 15/16 |  |  | 1.9370 | 1.9360 | 1.9375 | 0.5000 X 0.2500 |  |  |  |  | Yes |  | Size=3000; Design=5800; Arrangement=8S; % Width=100.0; Discharge=BH; Rotation=CCW; CFM=4562; SP=6.15; BHP=7.1; RPM=1770; Max Temp F=650; Effective Wheel Dia=32 1/2; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.135 (10); Hub=23-5-423; Coupling=FALK T10; Blades=10; Shaft Dia=1 15/16; Brg Centers=12; Critical Speed RPM=3591; BX=11 9/16; STB=6 1/8; OH=8.06; STH=1.38; Bearing Size=1 15/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=254T; Drive=Direct | Open
414668 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 414667 | 3000 | 5800 |  |  | 8S | 100.0 | BH | CCW | 32 1/2 | 4562 | 6.15 | 7.1 | 1770 | 500 | 650 | 0.0347 | 15.0 | 1800 | 15315 | 1 15/16 | 12 | 3591 | 27 13/16 | 8.06 | 11 9/16 | 6 1/8 | 23 | 1.38 | 1 15/16 | LINK BELT SERIES 300 | 400000 | FIXED | -54 | FIXED | 198 | 46 | 84 | 2872 | 1045 STEEL | 0.24 | 0.11 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) |  |  |  | 10 | 3709 | [8 empty] | 254T |  |  | 230 | 10 GA C.Q. HRS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 1.172 |  | Included |  | Included | 1241 | 43971 | 23-5-423 | FALK T10 | Direct |  |  |  |  | Yes | [5 empty] | 1 15/16 |  |  | 1.9370 | 1.9360 | 1.9375 | 0.5000 X 0.2500 |  |  |  |  | Yes |  | Size=3000; Design=5800; Arrangement=8S; % Width=100.0; Discharge=BH; Rotation=CCW; CFM=4562; SP=6.15; BHP=7.1; RPM=1770; Max Temp F=650; Effective Wheel Dia=32 1/2; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.135 (10); Hub=23-5-423; Coupling=FALK T10; Blades=10; Shaft Dia=1 15/16; Brg Centers=12; Critical Speed RPM=3591; BX=11 9/16; STB=6 1/8; OH=8.06; STH=1.38; Bearing Size=1 15/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=254T; Drive=Direct | Open
414686 | HD-PFD-IAF | CHECK VISION | pdf_vision | QT RUN REV A.pdf |  |  | SN414686 | 4014 | 1903 |  | PACKAGED FORCED DRAFT FAN | 88 | 100.0 | CCW | CCW | 42 1/4 | 40000 | 12.00 | 117.4 | 1760 | 70 | 70 | 0.0733 | 125.0 | 1800 | 19916 | 2 7/16 | 14 | 3489 | 32 9/16 | 8.39 | 17 1/8 | 8 | 43 | 2.50 | 2 7/16 | LINK BELT SERIES 300 | 400000 | FIXED | -96 | FIXED | 434 | 96 | 378 | 2088 | 1045 STEEL | 0.44 | 0.39 |  |  | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 1/4 |  |  | CAST IRON | 10 | 2088 | 2610 | [7 empty] | 444T |  | TEFC | 1893 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 8.828 |  |  |  | Included |  |  | HUB 19-5-1 | FALK T10, SIZE 1090T, BORE 2.438 | Direct |  |  |  |  | Yes | [5 empty] | 2 7/16 | [10 empty] | Yes | Ambient Temp F=90; Bore=2 7/16 | Size=4014; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=88; % Width=100.0; Discharge=CCW; Rotation=CCW; CFM=40000; SP=12.00; BHP=117.4; RPM=1760; Max Temp F=70; Effective Wheel Dia=42 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Wheel Material=CAST IRON; Hub=HUB 19-5-1; Coupling=FALK T10, SIZE 1090T, BORE 2.438; Blades=10; Shaft Dia=2 7/16; Brg Centers=14; Critical Speed RPM=3489; BX=17 1/8; STB=8; OH=8.39; STH=2.50; Bearing Size=2 7/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=444T; Motor Enclosure=TEFC; Drive=Direct | Open
414788 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN-REV.A.pdf |  |  | 414788 | 5414 | 5500 |  |  | 8S1 | 100.0 | TH | CCW | 56 1/4 | 45000 | 38.00 | 337.1 | 1780 | 120 | 120 | 0.0647 | 400.0 | 1800 | 26507 | 3 7/16 | 16 | 4967 | 37 3/4 | 8.47 | 15 15/16 | 10 1/8 | 99 | 2.19 | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -168 | FLOAT | 783 | 0 | 1205 | 2037 | 1045 STEEL | 0.48 | 0.47 |  |  | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A572 X-TEN | 5/16 |  |  |  | 16 | 2037 | [8 empty] | 449 |  | ODP | 3218 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 19 IN. CENTERS | 7.701 |  |  |  |  | 10299 | 140468 | 23-5-424 | FALK T10 | Direct |  | Required | [8 empty] | 3 7/16 |  |  | 3.4370 | 3.4355 | 3.4375 | 0.8750 X 0.4375 | 74 | 23 5/16 | 1 | SK-55-11 | Yes | Ambient Temp F=70 | Size=5414; Design=5500; Arrangement=8S1; % Width=100.0; Discharge=TH; Rotation=CCW; CFM=45000; SP=38.00; BHP=337.1; RPM=1780; Max Temp F=120; Effective Wheel Dia=56 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=23-5-424; Coupling=FALK T10; Blades=16; Shaft Dia=3 7/16; Brg Centers=16; Critical Speed RPM=4967; BX=15 15/16; STB=10 1/8; OH=8.47; STH=2.19; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=449; Motor Enclosure=ODP; Drive=Direct | Open
414804 | HDX | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 414804 | 4900 | 1904 |  |  | 7S1 | 90.0 | DB | CW | 53 7/8 | 52668 | 30.30 | 308.7 | 1785 | 140 | 180 | 0.0624 | 350.0 | 1800 | 25400 | 4 11/16 | 69 | 2681 |  |  |  | 9.38 |  | 2.94 | 3 3/16 | LINK BELT SERIES 6800 | 136667 | FIXED | 832 | FLOAT | 320 | 0 | 1769 | 1874 | 1045 STEEL | 0.20 | 0.55 |  |  | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A572 X-TEN | 1/2 |  |  |  | 10 | 1903 | 2720 | [7 empty] | 449T |  |  | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 12.597 |  | Included | 3.00 |  | 10398 | 138425 | 19-5-12 | FALK T10 | Direct |  |  |  | Yes | [9 empty] | 3.1870 | 3.1855 |  | 0.7500 X 0.3750 | 88 1/4 | 18 3/4 | 1082 | SK-19-72 | Yes | Ambient Temp F=70 | Size=4900; Design=1904; Arrangement=7S1; % Width=90.0; Discharge=DB; Rotation=CW; CFM=52668; SP=30.30; BHP=308.7; RPM=1785; Max Temp F=180; Effective Wheel Dia=53 7/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 ( 7); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Hub=19-5-12; Coupling=FALK T10; Blades=10; Shaft Dia=4 11/16; Brg Centers=69; Critical Speed RPM=2681; STB=9.38; STH=2.94; Bearing Size=3 3/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=449T; Drive=Direct | Open
414866 | HD-PFD-IAF | OK | cbc_qt_run_text | 414866 QT RUN WITH DIMENSIONS.txt |  |  | 414866 | 4900 | 1903 |  |  | 8S | 75.0 | TH | CW | 51 7/16 | 40023 | 31.00 | 236.2 | 1770 | 70 | 70 | 0.0750 | 250.0 | 1800 | 24245 | 3 15/16 | 16 | 5010 | 38 11/16 | 10.14 | 20 1/16 | 10 1/8 | 134 | 2.94 | 3 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -206 | FLOAT | 918 | 0 | 1140 | 2000 | 1045 STEEL | 0.21 | 0.19 | 30 5/8 |  | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A572 X-TEN | 3/8 |  |  |  | 10 | 2114 | 2640 | [7 empty] | 449T |  |  | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 11.870 |  |  |  | Yes | 7660 | 80871 | 19-5-289 | FALK T10 | Direct |  |  |  |  | Yes | [5 empty] | 3 15/16 |  |  | 3.9370 | 3.9355 | 3.9375 | 1.0000 X 0.5000 |  |  |  | SK-19-72 | Yes | Ambient Temp F=70; Discharge Height (A)=55 13/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=36 1/2; Base Width (F)=66 1/4; Shaft Height (H)=46 7/16; Total Vert Height (TV)=104 1/4; Max Right of CL to Hsg (RH)=36 1/2; Max Left of CL to Disch (LH)=48 1/8; Base Flange to CL (D)=92 13/16; Drive End of Shaft to CL (K)=46 3/16; Mtg Flange to CL (LR)=17 7/32 | Size=4900; Design=1903; Arrangement=8S; % Width=75.0; Discharge=TH; Rotation=CW; CFM=40023; SP=31.00; BHP=236.2; RPM=1770; Max Temp F=70; Effective Wheel Dia=51 7/16; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 ( 7); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Hub=19-5-289; Coupling=FALK T10; Blades=10; Shaft Dia=3 15/16; Brg Centers=16; Critical Speed RPM=5010; BX=20 1/16; STB=10 1/8; OH=10.14; STH=2.94; Bearing Size=3 15/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=30 5/8; Motor Frame=449T; Drive=Direct | Open
414890 | GENERAL LINE | OK | pdf_vision | QT RUN - UPDATED PER FEA.pdf |  |  | SN#414890 | 3000 | 6195 |  |  | 9H | 100.0 | UB | CW | 28 1/2 | 17350 | 15.00 | 50.2 | 2561 | 70 | 70 | 0.0659 | 60.0 | 2586 | 19295 | 2 11/16 | 12 | 5707 | 32 11/16 | 8.10 | 14 | 11 1/8 | 53 | 1.94 | 2 11/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 973 | FIXED | 281 | 125 | 152 | 3200 | 1045 STEEL | 0.13 | 0.35 |  |  | ASTM A6 XF-100 | 3/16 | ASTM A6 XF-100 | 3/16 | ASTM A572 X-TEN | 3/8 |  |  | CAST IRON | 10 |  | 6980 | [5 empty] | 6.0 | 3.0 | 364T | Z |  | 139 | 10 GA C.Q. HRS | SK-9-236 HT PRESSURE, 22 IN. CENTERS | 4.858 |  |  |  | Yes | 2200 | 59883 | 2 11/16 |  | Belt | Required |  | Yes |  | Yes | [5 empty] | 2 11/16 | [10 empty] | Yes | Ambient Temp F=70 | Size=3000; Design=6195; Arrangement=9H; % Width=100.0; Discharge=UB; Rotation=CW; CFM=17350; SP=15.00; BHP=50.2; RPM=2561; Max Temp F=70; Effective Wheel Dia=28 1/2; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=3/16; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Wheel Material=CAST IRON; Hub=2 11/16; Blades=10; Shaft Dia=2 11/16; Brg Centers=12; Critical Speed RPM=5707; BX=14; STB=11 1/8; OH=8.10; STH=1.94; Bearing Size=2 11/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=364T; Motor Position=Z; Drive=Belt | Open
414938 | HD-PFD-IAF | OK | cbc_qt_run_text | 414938 quote run.txt |  |  | 414938 | 4014 | 1904 |  | PACKAGED FORCED DRAFT FAN | 4S | 65.0 | DB | CW | 44 1/4 | 18980 | 23.62 | 94.1 | 1770 | 80 | 110 | 0.0728 | 100.0 | 1800 | 20864 | [8 empty] | 2.50 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 5/16 |  |  |  | 10 | 2228 | 2790 | 292 | 292 | 468 | 4.03 | 7.25 |  |  | 405T |  |  | 1260 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 7.755 |  | Not included |  | Yes |  |  | 19-5-16 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 7/8 | [9 empty] | SK-19-72 |  | Ambient Temp F=90 | Size=4014; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S; % Width=65.0; Discharge=DB; Rotation=CW; CFM=18980; SP=23.62; BHP=94.1; RPM=1770; Max Temp F=110; Effective Wheel Dia=44 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=5/16; Hub=19-5-16; Blades=10; STH=2.50; Motor Frame=405T; Drive=Motor mounted | Open
415041 | HD-PFD-IAF | OK | cbc_qt_run_text | 415041 QT RUN.txt |  |  | 415041 | 4014 | 1904 |  | PACKAGED FORCED DRAFT FAN | 4S1 | 50.0 | DB | CW | 44 1/4 | 16389 | 18.50 | 68.7 | 1770 | 138 | 138 | 0.0648 | 75.0 | 1800 | 20864 | [8 empty] | 2.50 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 5/16 |  |  |  | 10 | 2294 | 2870 | 256 | 292 | 443 | 3.56 | 4.75 |  |  | 365T |  |  | 920 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 7.278 |  | Not included |  |  |  |  | 19-5-1057 |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q1 BUSHING 2 3/8 |  |  |  |  | 73 | 15 9/16 | 1 | SK-19-72 |  | Ambient Temp F=90 | Size=4014; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S1; % Width=50.0; Discharge=DB; Rotation=CW; CFM=16389; SP=18.50; BHP=68.7; RPM=1770; Max Temp F=138; Effective Wheel Dia=44 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=5/16; Hub=19-5-1057; Blades=10; STH=2.50; Motor Frame=365T; Drive=Motor mounted | Open
415158 | HDX | CHECK VISION | pdf_vision | QT RUN REV C.pdf |  |  | SN#415158 | 7300 | 6195 |  |  | 781 | 105.0 | 90 | CCW | 69 3/8 | 118622 | 7.78 | 193.9 | 1186 | 700 | 800 | 0.0327 | 200.0 | 1200 | 21787 | 8 | 117 11/16 | 1995 |  |  |  | 10.00 |  | 3.88 | 3 15/16 | 6800 | 250187 | FIXED | 2287 | FLOAT | 1077 | 0 | 7530 | 1215 | 1045 STEEL | 0.16 | 0.26 |  |  | ASTM A6 | 1/4 | ASTM A6 | 3/16 | ASTM A572 | 1/2 | CAST STEEL |  | WR2 | 10 | 1215 | 1640 | [7 empty] | 449T |  | ODP | 2600 | 1/4 C.Q. HRS |  | 29.396 |  | Included | 4.00 |  | 21758 | 339117 | 19-5-1640 | FALK T10, SIZE 1100T | Direct | Required |  | Yes | Yes | Yes | [8 empty] | 3.4370 | 3.4355 |  | 0.8750 X 0.4375 | 131 1/2 | 27 7/8 | 90 |  | Yes | Ambient Temp F=70 | Size=7300; Design=6195; Arrangement=781; % Width=105.0; Discharge=90; Rotation=CCW; CFM=118622; SP=7.78; BHP=193.9; RPM=1186; Max Temp F=800; Effective Wheel Dia=69 3/8; Blade Material=ASTM A6; Blade Gauge=1/4; Sideplate Material=ASTM A6; Sideplate Gauge=3/16; Backplate Material=ASTM A572; Backplate Gauge=1/2; Liner Material=CAST STEEL; Wheel Material=WR2; Hub=19-5-1640; Coupling=FALK T10, SIZE 1100T; Blades=10; Shaft Dia=8; Brg Centers=117 11/16; Critical Speed RPM=1995; STB=10.00; STH=3.88; Bearing Size=3 15/16; Bearing Series=6800; Motor Frame=449T; Motor Enclosure=ODP; Drive=Direct | Open
415158 | HDX | UNRECOGNIZED FORMAT | unknown | OUTLET DAMPER QT RUN.doc | DAMPER | [104 empty] | Open
415191 | GENERAL LINE | OK | cbc_qt_run_text | 415191 QUOTE RUN.txt |  |  | 415191 | 33 | B10 | 4 |  | 9H | 100.0 | BH | CCW |  | 20000 | 3.00 | 28.0 | 1344 | 800 | 800 | 0.0340 | 40.0 | 1344 | 12529 | 3 3/16 | 24 | 2259 | 52 | 16.00 | 24 1/2 | 10 1/2 |  | 3.19 | 3 3/16 | LINK BELT SERIES 6800 | 400000 | FIXED | 404 | FLOAT | 395 | 0 | 239 | 1807 | 1045 STEEL | 0.25 | 0.18 |  |  | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A572 X-TEN | 1/4 |  |  |  | 12 | 2091 | [6 empty] | 11.4 | 3.2 | 324T | Z |  | 550 | 10 GA C.Q. HRS | SK-9-236 LOW PRESSURE, 36 IN. CENTERS | 6.510 | [6 empty] | 19-5-11 |  | Belt | Required |  |  |  | Yes | [5 empty] | 3 3/16 | [10 empty] | Yes | Ambient Temp F=90 | Size=33; Design=B10; Arrangement=9H; % Width=100.0; Discharge=BH; Rotation=CCW; Class=4; CFM=20000; SP=3.00; BHP=28.0; RPM=1344; Max Temp F=800; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=19-5-11; Blades=12; Shaft Dia=3 3/16; Brg Centers=24; Critical Speed RPM=2259; BX=24 1/2; STB=10 1/2; OH=16.00; STH=3.19; Bearing Size=3 3/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=324T; Motor Position=Z; Drive=Belt | Open
415267 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN - REV.A.pdf |  |  | 415267 | 5414 | 5800 |  |  | 8S | 100.0 | UB | CCW | 54 3/4 | 22325 | 23.00 | 121.8 | 1780 | 403 | 600 | 0.0413 | 150.0 | 1800 | 25800 | 3 7/16 | 16 | 3482 | 39 3/4 | 11.52 | 18 7/16 | 9 3/8 | 105 | 2.50 | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -233 | FLOAT | 806 | 0 | 1018 | 2122 | 1045 STEEL | 0.31 | 0.19 |  |  | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A572 X-TEN | 5/16 |  |  |  | 10 | 2122 | [8 empty] | 445T |  |  | 1785 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 19 IN. CENTERS | 3.842 |  | Included |  | Included | 6617 | 105908 | 49-5-145- | FALK T10 | Direct |  | Required |  |  | Yes | [5 empty] | 3 7/16 |  |  | 3.4370 | 3.4355 | 3.4375 | 0.8750 X 0.4375 |  |  |  |  | Yes |  | Size=5414; Design=5800; Arrangement=8S; % Width=100.0; Discharge=UB; Rotation=CCW; CFM=22325; SP=23.00; BHP=121.8; RPM=1780; Max Temp F=600; Effective Wheel Dia=54 3/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=49-5-145-; Coupling=FALK T10; Blades=10; Shaft Dia=3 7/16; Brg Centers=16; Critical Speed RPM=3482; BX=18 7/16; STB=9 3/8; OH=11.52; STH=2.50; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=445T; Drive=Direct | Open
415340 | HDX | OK | pdf_vision | QT RUN.pdf |  |  | SN#415340 | 5414 | 5500 |  |  | 7S1 | 100.0 | 100.0 PCT | DISCH TH, ROT CW, BOX 0 | 50 1/2 | 40713 | 30.00 | 244.4 | 1785 | 100 | 125 | 0.0685 | 250.0 | 1800 | 23798 | 3 3/16 | 53 | 2686 | 65.12 | 43.19 | 10.52 | 18.06 | 9.00 | 3.00 | 2 11/16 | LINK BELT SERIES 6800 | 230877 | FIXED | 463 | FLOAT | 139 | 0 |  | 2036 | 1045 STEEL | 0.39 | 0.61 |  |  | ASTM A1011-HSLAS | 0.179 (7) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A572 X-TEN | 5/16 |  |  | CAST STEEL | 16 | 2036 | [8 empty] | 449T |  |  | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS |  |  | Included | 3.00 |  |  |  | 23-5-424 | FALK T10, SIZE 1100T, BORE 2 11/16 NOT INCL. | DRIVE-FIXED |  |  |  | Yes | Yes | [8 empty] | 2.6870 | 2.6860 |  | 0.6250 X 0.3125 | 74 | 23 5/16 | 3119 | SK-55-11 | Yes | Ambient Temp F=90 | Size=5414; Design=5500; Arrangement=7S1; % Width=100.0; Discharge=100.0 PCT; Rotation=DISCH TH, ROT CW, BOX 0; CFM=40713; SP=30.00; BHP=244.4; RPM=1785; Max Temp F=125; Effective Wheel Dia=50 1/2; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 (7); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Wheel Material=CAST STEEL; Hub=23-5-424; Coupling=FALK T10, SIZE 1100T, BORE 2 11/16 NOT INCL.; Blades=16; Shaft Dia=3 3/16; Brg Centers=53; Critical Speed RPM=2686; BX=10.52; STB=18.06; OH=43.19; STH=3.00; Bearing Size=2 11/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=449T; Drive=DRIVE-FIXED | Open
415510 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 415510 | 13 | 52 |  |  | 1S | 65.0 | UB | CW | 22 5/8 | 3200 | 7.00 | 6.6 | 1750 | 73 | 150 | 0.0750 | 7.5 | 1750 | 10366 | 1 3/16 | 16 | 2441 | 26 3/16 | 7.04 | 9 7/16 | 4 7/8 | 9 | 0.60 | 1 3/16 | LINK BELT SERIES 200 | 400000 | FIXED | -6 | FIXED | 62 | 23 | 12 | 2034 | 1045 STEEL | 0.31 | 0.22 |  |  | ASTM A1011 CS | 0.135 (10) |  |  | ASTM A1011 CS | 0.135 (10) |  |  |  | 6 | 2064 | 5990 | [21 empty] | FALK G20 | Direct |  |  |  |  | Yes | [5 empty] | 1 3/16 | [11 empty] | Ambient Temp F=90 | Size=13; Design=52; Arrangement=1S; % Width=65.0; Discharge=UB; Rotation=CW; CFM=3200; SP=7.00; BHP=6.6; RPM=1750; Max Temp F=150; Effective Wheel Dia=22 5/8; Blade Material=ASTM A1011 CS; Blade Gauge=0.135 (10); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.135 (10); Coupling=FALK G20; Blades=6; Shaft Dia=1 3/16; Brg Centers=16; Critical Speed RPM=2441; BX=9 7/16; STB=4 7/8; OH=7.04; STH=0.60; Bearing Size=1 3/16; Bearing Series=LINK BELT SERIES 200; Drive=Direct | Open
415522 | HD-PFD-IAF | OK | cbc_qt_run_text | quote run 11-7-24.txt |  |  | 415522 | 4014 | 1904 |  | PACKAGED FORCED DRAFT FAN | 4S1 | 90.0 | DB | CW | 44 1/4 | 29870 | 20.00 | 117.7 | 1770 | 134 | 134 | 0.0649 | 150.0 | 1800 | 20864 | [8 empty] | 2.50 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 5/16 |  |  |  | 10 | 2130 | 2660 | 310 | 292 | 508 | 4.67 | 6.38 |  |  | 445T |  | TEFC | 2231 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 8.510 |  | Not included |  |  |  |  | 19-5-16 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 3 3/8 | [6 empty] | 73 | 15 9/16 | 1 |  |  | Ambient Temp F=90 | Size=4014; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S1; % Width=90.0; Discharge=DB; Rotation=CW; CFM=29870; SP=20.00; BHP=117.7; RPM=1770; Max Temp F=134; Effective Wheel Dia=44 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=5/16; Hub=19-5-16; Blades=10; STH=2.50; Motor Frame=445T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
415602 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.txt |  |  | 415602 | 4014 | 1904 |  | PACKAGED FORCED DRAFT FAN | 4S | 100.0 | DB | CW | 44 1/4 | 30380 | 19.80 | 117.0 | 1770 | 150 | 150 | 0.0600 | 125.0 | 1800 | 20864 | [8 empty] | 2.50 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 5/16 |  |  |  | 10 | 2095 | 2620 | 317 | 292 | 525 | 4.95 | 6.38 |  |  | 444T |  | TEFC | 1893 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 8.828 |  | Not included |  | Yes |  |  | 19-5-16 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 3 3/8 | [9 empty] | SK-19-72 |  | Ambient Temp F=90 | Size=4014; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S; % Width=100.0; Discharge=DB; Rotation=CW; CFM=30380; SP=19.80; BHP=117.0; RPM=1770; Max Temp F=150; Effective Wheel Dia=44 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=5/16; Hub=19-5-16; Blades=10; STH=2.50; Motor Frame=444T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
415689 | GENERAL LINE | OK | cbc_qt_run_text | 415689 QUOTE RUN.docx |  |  | 415689 | 26 | 16A | 4 |  | 8S | 85.0 | BAU | CW | 45 1/8 | 12130 | 32.00 | 92.0 | 1780 | 86 | 86 | 0.0603 | 100.0 | 1800 | 21265 | 3 7/16 | 19 | 3544 | 44 1/16 | 13.00 | 13 3/4 | 8 1/8 |  |  | 3 7/16 | LINK BELT SERIES 300 | 400000 | FIXED | -106 | FIXED | 519 | 0 | 257 | 2039 | A240 304 SS | 0.14 | 0.10 |  |  | ASTM A240 304L SS | 1/4 | [7 empty] | 6 | 2039 | 10200 | [21 empty] | FALK T10 | Direct |  |  | Yes |  | Yes | [5 empty] | 3 7/16 | [11 empty] | Ambient Temp F=86 | Size=26; Design=16A; Arrangement=8S; % Width=85.0; Discharge=BAU; Rotation=CW; Class=4; CFM=12130; SP=32.00; BHP=92.0; RPM=1780; Max Temp F=86; Effective Wheel Dia=45 1/8; Blade Material=ASTM A240 304L SS; Blade Gauge=1/4; Coupling=FALK T10; Blades=6; Shaft Dia=3 7/16; Brg Centers=19; Critical Speed RPM=3544; BX=13 3/4; STB=8 1/8; OH=13.00; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 300; Drive=Direct | Open
415861 | GENERAL LINE | OK | cbc_qt_run_text | 358-24-2748 - QT RUN.pdf |  |  | 415861 | 20 | 36 |  |  | 9H | 100.0 | UB | CW |  | 8100 | 10.00 | 19.5 | 2544 | 70 | 70 | 0.0750 | 25.0 | 2544 | 14373 | 1 11/16 | 10 | 4847 | 26 9/16 | 8.27 | 13 5/16 | 5 7/8 | 17 | 2.04 | 1 11/16 | LINK BELT SERIES 300 | 121116 | FIXED | 341 | FIXED | 73 | 0 | 10 | 2747 | 1045 STEEL | 0.18 | 0.36 |  |  | ALUM 5052-H32 | 0.190 | ALUM 3003-O | 0.125 | ALUM 5052-H32 | 0.190 |  |  |  | 12 | 2747 | 6810 | [5 empty] | 6.0 | 3.0 |  |  | TEFC | [10 empty] | 4-5-14 |  | Belt |  |  |  |  | Yes | [17 empty] | Ambient Temp F=70 | Size=20; Design=36; Arrangement=9H; % Width=100.0; Discharge=UB; Rotation=CW; CFM=8100; SP=10.00; BHP=19.5; RPM=2544; Max Temp F=70; Blade Material=ALUM 5052-H32; Blade Gauge=0.190; Sideplate Material=ALUM 3003-O; Sideplate Gauge=0.125; Backplate Material=ALUM 5052-H32; Backplate Gauge=0.190; Hub=4-5-14; Blades=12; Shaft Dia=1 11/16; Brg Centers=10; Critical Speed RPM=4847; BX=13 5/16; STB=5 7/8; OH=8.27; STH=2.04; Bearing Size=1 11/16; Bearing Series=LINK BELT SERIES 300; Motor Enclosure=TEFC; Drive=Belt | Open
415889 | GENERAL LINE | OK | cbc_qt_run_text | quote run.txt |  |  | 415889 | 29 | 16A | 3 |  | 8S | 100.0 | TH | CCW | 50 1/2 | 27483 | 16.49 | 123.8 | 1173 | 97 | 97 | 0.0711 | 150.0 | 1200 |  | 3 3/16 | 30 | 1821 | 59 11/16 | 17.14 | 17 1/8 | 8 1/2 | 135 |  | 3 3/16 | LINK BELT SERIES 300 | 400000 | FIXED | -85 | FIXED | 545 | 0 | 414 | 1517 | 1045 STEEL | 0.37 | 0.32 | [10 empty] | A242 CORTEN | 6 | 1924 | [22 empty] | FALK T10 | Direct |  |  |  |  | Yes | [5 empty] | 3 3/16 | [11 empty] | Ambient Temp F=70 | Size=29; Design=16A; Arrangement=8S; % Width=100.0; Discharge=TH; Rotation=CCW; Class=3; CFM=27483; SP=16.49; BHP=123.8; RPM=1173; Max Temp F=97; Effective Wheel Dia=50 1/2; Wheel Material=A242 CORTEN; Coupling=FALK T10; Blades=6; Shaft Dia=3 3/16; Brg Centers=30; Critical Speed RPM=1821; BX=17 1/8; STB=8 1/2; OH=17.14; Bearing Size=3 3/16; Bearing Series=LINK BELT SERIES 300; Drive=Direct | Open
415956 | HD-PFD-IAF | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | SN415956 | 4900 | DESIGN 1902 |  |  | ARR 88 | 90.0 | DISCH BH | ROT CW | 3370 CPM | 49711 | 21.43 | 204.6 | 1770 | 100 | 100 F | 0.0685 | 250.0 | 1800 | 23091 | 3 7/16 | 16 | 3629 | 38 1/4 | 10.02 | 20 13/16 | 9 7/8 | 2.94 | M1.5 | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -270 | FLOAT | 1035 | 0 | 1326 | 1872 | 1045 STEEL | 0.41 | 0.29 |  |  | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.179 (7) | ASTM A572 X-TEN | 1/2 |  |  | CAST IRON | 10 | 1872 | 3370 | [7 empty] | 449T |  | ODP | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS |  |  |  |  | Included | 8456 | 99994 | 3/16 | FALK T10, SIZE 110OT, BORE 3.438 | RUN TEST AT FACTORY |  |  |  | Yes | Yes | [5 empty] | 3 3/16 | [9 empty] | SK-19-72 | Yes | Ambient Temp F=90; Manufacturer=JOHN ZINK COMPANY; Model=1902 PFD | Size=4900; Design=DESIGN 1902; Arrangement=ARR 88; % Width=90.0; Discharge=DISCH BH; Rotation=ROT CW; CFM=49711; SP=21.43; BHP=204.6; RPM=1770; Max Temp F=100 F; Effective Wheel Dia=3370 CPM; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 (7); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Wheel Material=CAST IRON; Hub=3/16; Coupling=FALK T10, SIZE 110OT, BORE 3.438; Blades=10; Shaft Dia=3 7/16; Brg Centers=16; Critical Speed RPM=3629; BX=20 13/16; STB=9 7/8; OH=10.02; STH=M1.5; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=449T; Motor Enclosure=ODP; Drive=RUN TEST AT FACTORY | Open
415970 | GENERAL LINE | OK | cbc_qt_run_text | QT Run 415970 - Markup per FEA.docx |  | hub | 415970 | 5414 | 6195 |  |  | 8S | 95.0 | BAU | CW | 51 9/16 | 75000 | 16.00 | 244.3 | 1785 | 300 | 300 | 0.0520 | 250.0 | 1800 | 24287 | 4 3/16 | 16 | 3112 | 43 7/16 | 14.34 | 26 7/16 | 10 1/2 |  | 3.38 | 4 3/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -542 | FLOAT | 1547 | 0 | 1909 | 1849 | 1045 STEEL | 0.26 | 0.18 | 36 1/2 |  | ASTM A656 HI-FORM | 3/16 | GA. ASTM A1011-HSLA | 7 | ASTM CQ HRS A36 | 1/2 |  |  |  | 10 | 1849 | 3140 | [7 empty] | 449T |  |  | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 15.652 |  | Included |  | Yes | 10071 | 135524 |  | FALK T10 | Direct |  |  | Yes |  | Yes | [8 empty] | 3.937 | 3.935 | 3.9375 | 1.0000 X 0.5000 |  |  |  | SK-19-72 | Yes | Ambient Temp F=70; Discharge Height (A)=61 3/4; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=40 3/8; Base Width (F)=72 1/2; Shaft Height (H)=66 1/4; Total Vert Height (TV)=105 7/8; Max Right of CL to Hsg (RH)=48 11/16; Max Left of CL to Disch (LH)=73 5/8; Base Flange to CL (D)=99 7/8; Drive End of Shaft to CL (K)=52 15/16; Mtg Flange to CL (LR)=20 1/2 | Size=5414; Design=6195; Arrangement=8S; % Width=95.0; Discharge=BAU; Rotation=CW; CFM=75000; SP=16.00; BHP=244.3; RPM=1785; Max Temp F=300; Effective Wheel Dia=51 9/16; Blade Material=ASTM A656 HI-FORM; Blade Gauge=3/16; Sideplate Material=GA. ASTM A1011-HSLA; Sideplate Gauge=7; Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/2; Coupling=FALK T10; Blades=10; Shaft Dia=4 3/16; Brg Centers=16; Critical Speed RPM=3112; BX=26 7/16; STB=10 1/2; OH=14.34; STH=3.38; Bearing Size=4 3/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=36 1/2; Motor Frame=449T; Drive=Direct | Open
415970 | GENERAL LINE | UNRECOGNIZED FORMAT | unknown | damper quote run.doc | DAMPER | [104 empty] | Open
416091 | GENERAL LINE | OK | d64_wheel_construction | D64 Wheel Construction (Inner Ring)- 300-24-307 (1) CHANGED.xlsx | [103 empty] | Fan Size=150; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=25000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.1345 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=150; Outer Ring Thickness=0.1345; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=25000 | Open
416104 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 416069 | 4900 | 5500 |  |  | 8S | 100.0 | BH | CW | 50 1/4 | 26936 | 28.60 | 161.9 | 1770 | 190 | 190 | 0.0608 | 200.0 | 1800 | 23680 | 2 15/16 | 16 | 5004 | 35 3/16 | 7.76 | 14 1/8 | 8 3/4 | 68 | 2.00 | 2 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -73 | FLOAT | 472 | 0 | 566 | 2371 | 1045 STEEL | 0.42 | 0.41 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 16 | 2371 | [8 empty] | 447T |  |  | 2280 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 6.293 |  | Included |  | Included | 6142 | 83575 | 49-5-145- | FALK T10 | Direct |  |  |  |  | Yes | [5 empty] | 2 15/16 |  |  | 2.9370 | 2.9355 | 2.9375 | 0.7500 X 0.3750 |  |  |  |  | Yes | Ambient Temp F=60 | Size=4900; Design=5500; Arrangement=8S; % Width=100.0; Discharge=BH; Rotation=CW; CFM=26936; SP=28.60; BHP=161.9; RPM=1770; Max Temp F=190; Effective Wheel Dia=50 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=49-5-145-; Coupling=FALK T10; Blades=16; Shaft Dia=2 15/16; Brg Centers=16; Critical Speed RPM=5004; BX=14 1/8; STB=8 3/4; OH=7.76; STH=2.00; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=447T; Drive=Direct | Open
416117 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 416117 | 4900 | 5500 |  |  | 4S1 | 100.0 | TH | CCW | 52 1/4 | 33420 | 33.20 | 221.0 | 1785 | 132 | 150 | 0.0641 | 250.0 | 1800 | 24622 | 2 11/16 | 16 | 4400 | 33 3/16 | 7.17 | 13 1/2 | 7 3/8 |  | 2.00 | 2 11/16 | LINK BELT SERIES 300 | 400000 | FIXED | -54 | FIXED | 472 | 401 | 641 | 1810 | 1045 STEEL | 0.87 | 0.63 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 16 | 2382 |  | 318 | 401 | 640 | 3.79 | 5.95 |  |  | 447T |  |  | 2280 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 6.293 |  | Not included |  |  | 6173 | 87276 | 49-5-145- | FALK G20 | Motor mounted |  |  |  | Yes | Yes | [5 empty] | 3 3/8 |  |  | 2.6870 | 2.6860 | 2.6875 | 0.6250 X 0.3125 | 66 3/4 | 21 1/16 | 1 |  | Yes | Ambient Temp F=70 | Size=4900; Design=5500; Arrangement=4S1; % Width=100.0; Discharge=TH; Rotation=CCW; CFM=33420; SP=33.20; BHP=221.0; RPM=1785; Max Temp F=150; Effective Wheel Dia=52 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=49-5-145-; Coupling=FALK G20; Blades=16; Shaft Dia=2 11/16; Brg Centers=16; Critical Speed RPM=4400; BX=13 1/2; STB=7 3/8; OH=7.17; STH=2.00; Bearing Size=2 11/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=447T; Drive=Motor mounted | Open
416118 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 416118 | 4900 | 5500 |  |  | 4S1 | 100.0 | TH | CW | 52 1/4 | 33420 | 33.20 | 221.0 | 1785 | 132 | 150 | 0.0641 | 250.0 | 1800 | 24622 | 2 11/16 | 16 | 4400 | 33 3/16 | 7.17 | 13 1/2 | 7 3/8 |  | 2.00 | 2 11/16 | LINK BELT SERIES 300 | 400000 | FIXED | -54 | FIXED | 472 | 401 | 641 | 1810 | 1045 STEEL | 0.87 | 0.63 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 16 | 2382 |  | 318 | 401 | 640 | 3.79 | 5.95 |  |  | 447T |  |  | 2280 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 6.293 |  | Not included |  |  | 6173 | 87273 | 49-5-145- | FALK G20 | Motor mounted |  |  |  | Yes | Yes | [5 empty] | 3 3/8 |  |  | 2.6870 | 2.6860 | 2.6875 | 0.6250 X 0.3125 | 66 3/4 | 21 1/16 | 1 |  | Yes | Ambient Temp F=70 | Size=4900; Design=5500; Arrangement=4S1; % Width=100.0; Discharge=TH; Rotation=CW; CFM=33420; SP=33.20; BHP=221.0; RPM=1785; Max Temp F=150; Effective Wheel Dia=52 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=49-5-145-; Coupling=FALK G20; Blades=16; Shaft Dia=2 11/16; Brg Centers=16; Critical Speed RPM=4400; BX=13 1/2; STB=7 3/8; OH=7.17; STH=2.00; Bearing Size=2 11/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=447T; Drive=Motor mounted | Open
416170 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.txt |  |  | 416170 | 4900 | 1902 |  |  | 4S | 90.0 | BH | CW |  | 43608 | 4.50 | 54.0 | 1185 | 120 | 120 | 0.0656 | 75.0 | 1200 | 15394 | [8 empty] | 2.94 | [15 empty] | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A572 X-TEN | 3/8 |  |  |  | 10 | 1932 | 2470 | 539 | 216 | 1150 | 5.88 | 7.32 |  |  | 405T |  |  | 1260 | 1/4 C.Q. HRS | SK-9-236 MED PRESSURE, 30 IN. CENTERS | 12.597 |  | Not included |  | Included | 4955 | 72837 | 19-5-289 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 7/8 | [11 empty] | Ambient Temp F=70 | Size=4900; Design=1902; Arrangement=4S; % Width=90.0; Discharge=BH; Rotation=CW; CFM=43608; SP=4.50; BHP=54.0; RPM=1185; Max Temp F=120; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 ( 7); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Hub=19-5-289; Blades=10; STH=2.94; Motor Frame=405T; Drive=Motor mounted | Open
416170 | HD-PFD-IAF | UNRECOGNIZED FORMAT | unknown | Outlet Damper Qt Run.doc | DAMPER | [104 empty] | Open
416180 | GENERAL LINE | OK | d64_wheel_construction | 909-24-3192 D64 Wheel Construction (Inner Ring).xlsx | [103 empty] | Fan Size=222; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=80000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.25 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=222; Outer Ring Thickness=0.25; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=80000 | Open
416194 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 416194 | 4900 | 6195 |  |  | 9H | 100.0 | UB | CW | 46 9/16 | 50000 | 16.00 | 158.0 | 1585 | 70 | 70 | 0.0750 | 200.0 | 1635 | 19925 | 3 7/16 | 16 | 3267 | 40 3/8 | 11.85 | 21 3/8 | 12 |  | 2.94 | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 2889 | FIXED | 762 | 357 | 1110 | 1733 | 1045 STEEL | 0.37 | 0.66 |  |  | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 |  |  |  | 10 | 1733 | 2220 | [5 empty] | 9.6 | 5.8 | 447T | W |  | 2280 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 13.033 |  | Included |  | Included | 6853 | 84894 | 19-5-289 |  | Belt | Required |  |  | Yes | Yes | [5 empty] | 3 3/16 | [9 empty] | SK-19-72 | Yes | Ambient Temp F=70 | Size=4900; Design=6195; Arrangement=9H; % Width=100.0; Discharge=UB; Rotation=CW; CFM=50000; SP=16.00; BHP=158.0; RPM=1585; Max Temp F=70; Effective Wheel Dia=46 9/16; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=19-5-289; Blades=10; Shaft Dia=3 7/16; Brg Centers=16; Critical Speed RPM=3267; BX=21 3/8; STB=12; OH=11.85; STH=2.94; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=447T; Motor Position=W; Drive=Belt | Open
416415 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN 1-27-2025.txt |  |  | 416415 | 4014 | 1904 |  | PACKAGED FORCED DRAFT FAN | 8S | 75.0 | BH | CCW | 44 1/4 | 24697 | 21.26 | 103.7 | 1770 | 100 | 125 | 0.0677 | 125.0 | 1800 | 20864 | 2 15/16 | 14 | 5188 | 32 5/8 | 7.78 | 16 3/16 | 8 1/4 | 63 | 2.50 | 2 15/16 | LINK BELT SERIES 300 | 400000 | FIXED | -96 | FIXED | 488 | 292 | 484 | 2137 | 1045 STEEL | 0.26 | 0.24 | 25 3/8 |  | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 5/16 |  |  |  | 10 | 2187 | 2730 | [7 empty] | 444T |  | TEFC | 1893 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 8.073 |  |  |  | Included |  |  | 19-5-16 | FALK T10 | Direct |  |  |  |  | Yes | [5 empty] | 2 15/16 |  |  | 2.9370 | 2.9355 | 2.9375 | 0.7500 X 0.3750 |  |  |  |  | Yes | Ambient Temp F=90; Discharge Height (A)=45 13/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=30; Base Width (F)=55; Shaft Height (H)=50 13/16; Total Vert Height (TV)=83 11/16; Max Right of CL to Hsg (RH)=30; Max Left of CL to Disch (LH)=39 9/16; Base Flange to CL (D)=74 9/16; Drive End of Shaft to CL (K)=38 7/16; Mtg Flange to CL (LR)=15 11/16 | Size=4014; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=8S; % Width=75.0; Discharge=BH; Rotation=CCW; CFM=24697; SP=21.26; BHP=103.7; RPM=1770; Max Temp F=125; Effective Wheel Dia=44 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=5/16; Hub=19-5-16; Coupling=FALK T10; Blades=10; Shaft Dia=2 15/16; Brg Centers=14; Critical Speed RPM=5188; BX=16 3/16; STB=8 1/4; OH=7.78; STH=2.50; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 300; Housing Width (N)=25 3/8; Motor Frame=444T; Motor Enclosure=TEFC; Drive=Direct | Open
416476 | GENERAL LINE | OK | cbc_qt_run_text | quote run.docx |  |  | 416476 | 22-1/4 | B10 | 4 |  | 8S | 90.0 | TH | CCW |  | 16000 | 21.00 | 78.3 | 3555 | 70 | 70 | 0.0750 | 100.0 | 3600 | 22627 | 2 3/16 | 14 | 4800 | 34 1/8 | 8.25 | 13 9/16 | 11 | 36 | 2.27 | 2 3/16 | LINK BELT SERIES 300 | 400000 | FIXED | -11 | FLOAT | 147 | 0 | 39 | 3650 | 1045 STEEL | 0.23 | 0.22 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 12 | 4303 | 5780 | [7 empty] | 405TS |  | TEFC | 1575 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 2.851 | [6 empty] | 19-5-26 | FALK T10 | Direct |  |  |  |  | Yes | [5 empty] | 2 3/16 | [10 empty] | Yes | Ambient Temp F=90 | Size=22-1/4; Design=B10; Arrangement=8S; % Width=90.0; Discharge=TH; Rotation=CCW; Class=4; CFM=16000; SP=21.00; BHP=78.3; RPM=3555; Max Temp F=70; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=19-5-26; Coupling=FALK T10; Blades=12; Shaft Dia=2 3/16; Brg Centers=14; Critical Speed RPM=4800; BX=13 9/16; STB=11; OH=8.25; STH=2.27; Bearing Size=2 3/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=405TS; Motor Enclosure=TEFC; Drive=Direct | Open
416486 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 416486 | 5414 | 6195 |  |  | 8S | 90.0 | BAU | CW | 51 9/16 | 75000 | 21.00 | 329.4 | 1770 | 70 | 70 | 0.0750 | 350.0 | 1800 | 24287 | 3 15/16 | 16 | 3629 | 39 5/8 | 12.01 | 22 11/16 | 10 1/8 | 137 | 3.38 | 3 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -386 | FLOAT | 1256 | 0 | 1757 | 1940 | 1045 STEEL | 0.30 | 0.26 | 35 7/8 |  | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  |  | 10 | 1940 | 2430 | [10 empty] | 3875 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 15.384 |  | Included |  | Included | 11325 | 125428 | 19-5-12 | FALK T10 | Direct |  | Required | Yes | [7 empty] | 3 15/16 |  |  | 3.9370 | 3.9355 | 3.9375 | 1.0000 X 0.5000 |  |  |  | SK-19-72 | Yes | Ambient Temp F=70; Discharge Height (A)=61 3/4; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=40 3/8; Base Width (F)=72 1/2; Shaft Height (H)=66 1/4; Total Vert Height (TV)=105 7/8; Max Right of CL to Hsg (RH)=48 11/16; Max Left of CL to Disch (LH)=73 5/8; Base Flange to CL (D)=102 3/4; Drive End of Shaft to CL (K)=48 13/16; Mtg Flange to CL (LR)=20 3/16 | Size=5414; Design=6195; Arrangement=8S; % Width=90.0; Discharge=BAU; Rotation=CW; CFM=75000; SP=21.00; BHP=329.4; RPM=1770; Max Temp F=70; Effective Wheel Dia=51 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=19-5-12; Coupling=FALK T10; Blades=10; Shaft Dia=3 15/16; Brg Centers=16; Critical Speed RPM=3629; BX=22 11/16; STB=10 1/8; OH=12.01; STH=3.38; Bearing Size=3 15/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=35 7/8; Drive=Direct | Open
416487 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 416487 | 5414 | 6195 |  |  | 8S | 90.0 | BAU | CCW | 51 9/16 | 75000 | 21.00 | 329.4 | 1770 | 70 | 70 | 0.0750 | 350.0 | 1800 | 24287 | 3 15/16 | 16 | 3629 | 39 5/8 | 12.01 | 22 11/16 | 10 1/8 | 137 | 3.38 | 3 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -386 | FLOAT | 1256 | 0 | 1757 | 1940 | 1045 STEEL | 0.30 | 0.26 | 35 7/8 |  | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  |  | 10 | 1940 | 2430 | [10 empty] | 3875 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 15.384 |  | Included |  | Included | 11325 | 125428 | 19-5-12 | FALK T10 | Direct |  | Required | Yes | [7 empty] | 3 15/16 |  |  | 3.9370 | 3.9355 | 3.9375 | 1.0000 X 0.5000 |  |  |  | SK-19-72 | Yes | Ambient Temp F=70; Discharge Height (A)=61 3/4; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=40 3/8; Base Width (F)=72 1/2; Shaft Height (H)=66 1/4; Total Vert Height (TV)=105 7/8; Max Right of CL to Hsg (RH)=73 5/8; Max Left of CL to Disch (LH)=48 11/16; Base Flange to CL (D)=102 3/4; Drive End of Shaft to CL (K)=48 13/16; Mtg Flange to CL (LR)=20 3/16 | Size=5414; Design=6195; Arrangement=8S; % Width=90.0; Discharge=BAU; Rotation=CCW; CFM=75000; SP=21.00; BHP=329.4; RPM=1770; Max Temp F=70; Effective Wheel Dia=51 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=19-5-12; Coupling=FALK T10; Blades=10; Shaft Dia=3 15/16; Brg Centers=16; Critical Speed RPM=3629; BX=22 11/16; STB=10 1/8; OH=12.01; STH=3.38; Bearing Size=3 15/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=35 7/8; Drive=Direct | Open
416730 | HDX | CHECK VISION | pdf_vision | QT Run.pdf |  |  | SN#416730 | 4900 | 1910 |  |  | 7S | 85.0 | TH | CW | 661 | 52956 | 28 | 274.0 | 1780 | 125 | 129 | 0.0620 | 300.0 | 1780 | 24638 | 3 3/16 | 51 11/16 | 1999 | 13.29 |  |  | 7.62 |  | 4.38 | 2 7/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 610 | FIXED | 223 | 626 |  | 1817 |  | 0.50 | 0.99 |  |  | CAST IRON | 19=5=222 | ASTM A1011-HSLAS | 0.179 (7) | ASTM CQ HRS A36 | 5/16 |  |  | CAST IRON | 12 | 2116 | 2660 | [7 empty] | 449T |  |  | 2600 | 3/8 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 13.590 |  |  |  | Included | 9049 | 130679 | CAST IRON | FALK G20, SIZE 1030G, BORE 2 7/16 | Direct |  |  |  | Yes | [9 empty] | 2.4370 | 2.4360 |  | 0.6250 X 0.3125 |  |  |  | SK-19-72 | Yes | Ambient Temp F=90 F; Replacement=#249287; Coupling Ref=SKE-9-357; Wheel Hub Nominal Bore=3.1875; Wheel Hub Max Bore=3.1890; Wheel Hub Min Bore=3.1880; Shrink Fit Max Shaft Dia=3.1920; Shrink Fit Min Shaft Dia=3.1910; Wheel Hub Keyway Width=0.7510 (MIN) - 0.7540 (MAX); Wheel Hub Keyway Depth=0.3750; Nom Shaft Bore at Fan Shaft Half Coupling=2.4375; Max Shaft Diameter at Fan Shaft Half Coupling=2.4370; Min Shaft Diameter at Fan Shaft Half Coupling=2.4360; Shrink Fit Max Half Coupling Bore=2.4355; Shrink Fit Min Half Coupling Bore=2.4345; Keyway Dimensions for Half Coupling=0.6250 X 0.3125; Set Gap=3/16; Number of Blades=12; Wheel Weight=18264; Residual CPM=2660 | Size=4900; Design=1910; Arrangement=7S; % Width=85.0; Discharge=TH; Rotation=CW; CFM=52956; SP=28; BHP=274.0; RPM=1780; Max Temp F=129; Effective Wheel Dia=661; Blade Material=CAST IRON; Blade Gauge=19=5=222; Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 (7); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=5/16; Wheel Material=CAST IRON; Hub=CAST IRON; Coupling=FALK G20, SIZE 1030G, BORE 2 7/16; Blades=12; Shaft Dia=3 3/16; Brg Centers=51 11/16; Critical Speed RPM=1999; STB=7.62; STH=4.38; Bearing Size=2 7/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=449T; Drive=Direct | Open
416736 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN REF ONLY SEE WHEEL READ ME!.txt |  |  | 416736 | 2412 | 6195 |  |  | 4S | 85.0 | UB | CW | 23 1/4 | 13000 | 16.00 | 45.1 | 3550 | 70 | 70 | 0.0750 | 50.0 | 3600 | 21936 | [8 empty] | 1.62 | [15 empty] | ALUM 5052-H32 | 0.190 | ALUM 3003-O | 0.250 | ALUM 5052-H32 | 0.250 |  |  |  | 10 | 3791 | 9130 | 54 | 108 | 23 | 3.06 | 4.12 |  |  | 326TS |  |  | 610 | 10 GA A240 316L SS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 3.104 |  | Not included |  | Included |  |  | 19-5-1056 |  | Motor mounted | Required |  |  |  | Yes | [7 empty] | Q2 BUSHING 1 7/8 | [9 empty] | Ambient Temp F=90 | Size=2412; Design=6195; Arrangement=4S; % Width=85.0; Discharge=UB; Rotation=CW; CFM=13000; SP=16.00; BHP=45.1; RPM=3550; Max Temp F=70; Effective Wheel Dia=23 1/4; Blade Material=ALUM 5052-H32; Blade Gauge=0.190; Sideplate Material=ALUM 3003-O; Sideplate Gauge=0.250; Backplate Material=ALUM 5052-H32; Backplate Gauge=0.250; Hub=19-5-1056; Blades=10; STH=1.62; Motor Frame=326TS; Drive=Motor mounted | Open
416775 | HDX | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 416729 | 4412 | 1910 |  |  | 8S1 | 105.0 | TH | CCW |  | 50334 | 24.40 | 230.1 | 1780 | 125 | 150 | 0.0655 | 250.0 | 1780 | 22375 | 2 15/16 | 16 | 2312 | 34 7/16 | 11.48 | 23 13/16 | 7 3/4 |  | 3.94 | 2 15/16 | LINK BELT SERIES 6800 | 353642 | FIXED | -325 | FLOAT | 1023 | 0 | 885 | 1849 | 1045 STEEL | 0.76 | 0.48 |  |  | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM CQ HRS A36 | 1/4 |  |  |  | 12 | 1943 | 2430 | [7 empty] | 449T |  |  | 2600 | 3/8 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 11.953 | 49.000 | Included |  |  | 10686 | 156354 | 19-5-222 | FALK G20 | Direct |  |  |  | Yes | Yes | [5 empty] | 2 11/16 |  |  | 2.9370 | 2.9355 | 2.9375 | 0.7500 X 0.3750 | 88 1/4 | 18 3/4 | 3 | SK-19-72 | Yes | Ambient Temp F=90 | Size=4412; Design=1910; Arrangement=8S1; % Width=105.0; Discharge=TH; Rotation=CCW; CFM=50334; SP=24.40; BHP=230.1; RPM=1780; Max Temp F=150; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 ( 7); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Hub=19-5-222; Coupling=FALK G20; Blades=12; Shaft Dia=2 15/16; Brg Centers=16; Critical Speed RPM=2312; BX=23 13/16; STB=7 3/4; OH=11.48; STH=3.94; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=449T; Drive=Direct | Open
416775 | HDX | OK | cbc_qt_run_text | QUOTE RUN.pdf |  |  | 416775 | 3300 | 1910 |  |  | 3D | 105.0 | UB | CCW |  | 40900 | 13.00 | 100.0 | 1780 | 110 | 110 | 0.0688 | 125.0 | 2070 | 19296 | 6 | 71 | 2995 |  |  |  | 13.00 | [5 empty] | FIXED | 441 | FLOAT | 381 | 0 | 373 | 2139 | 1045 STEEL | 0.04 | 0.23 |  |  | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | [6 empty] | 2375 | 3850 | [11 empty] | 3/16 C.Q. HRS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 11.437 |  |  |  | Yes | 3443 | 172711 | 19-5-127 | FALK T10 | Direct |  |  |  | Yes | [9 empty] | 2.9370 | 2.9355 | 2.9375 | 0.7500 X 0.3750 |  |  |  |  | Yes | Ambient Temp F=90 | Size=3300; Design=1910; Arrangement=3D; % Width=105.0; Discharge=UB; Rotation=CCW; CFM=40900; SP=13.00; BHP=100.0; RPM=1780; Max Temp F=110; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Hub=19-5-127; Coupling=FALK T10; Shaft Dia=6; Brg Centers=71; Critical Speed RPM=2995; STB=13.00; Drive=Direct | Open
416805 | HDX | OK | cbc_qt_run_text | 416805-QT RUN.txt |  |  | 416805 | 3612 | 4800 |  |  | 1S | 100.0 | TH | CCW |  | 24810 | 10.00 | 52.0 | 1752 | 400 | 400 | 0.0430 | 60.0 | 1752 | 16742 | 3 7/16 | 22 | 4680 | 51 1/8 | 10.75 | 17 1/2 | 15 5/8 |  | 1.50 | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 1003 | FIXED | 267 | 179 | 198 | 2106 | 1045 STEEL | 0.14 | 0.31 | 20 3/4 |  | ASTM A606 CORTEN | 0.179 ( 7) | ASTM A606 CORTEN | 0.135 (10) | ASTM A242 CORTEN | 1/4 |  |  |  | 12 | 2106 | 3380 | [5 empty] | 8.7 | 3.4 |  |  |  |  | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 4.908 |  |  |  | Included | 2084 | 57427 | 19-5-16 |  | Belt |  |  |  | Yes | Yes | [5 empty] | 3 3/16 | [10 empty] | Yes | Ambient Temp F=70; Discharge Height (A)=34 1/16; Bottom of Disch to CL (W)=7 3/4; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=29 1/4; Base Width (F)=46 1/4; Shaft Height (H)=33 1/16; Total Vert Height (TV)=76 7/8; Max Right of CL to Hsg (RH)=35 15/16; Max Left of CL to Disch (LH)=29 1/4; Base Flange to CL (D)=46 7/16; Drive End of Shaft to CL (K)=55 5/8; Mtg Angle To Cl (LL)=13 3/8 | Size=3612; Design=4800; Arrangement=1S; % Width=100.0; Discharge=TH; Rotation=CCW; CFM=24810; SP=10.00; BHP=52.0; RPM=1752; Max Temp F=400; Blade Material=ASTM A606 CORTEN; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A606 CORTEN; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A242 CORTEN; Backplate Gauge=1/4; Hub=19-5-16; Blades=12; Shaft Dia=3 7/16; Brg Centers=22; Critical Speed RPM=4680; BX=17 1/2; STB=15 5/8; OH=10.75; STH=1.50; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=20 3/4; Drive=Belt | Open
416809 | HDX | OK | pdf_vision | QT RUN-REV A-FEA.pdf |  |  | SN416809 | 6000 | 1910 |  |  | 7S1 | 75.0 | 0 | CCW |  | 96453 | 90 | 735.5 | 1780 | 133 | 150 | 0.0628 | 750.0 | 1800 | 30508 | 6 3/4 | 94 11/16 | 2485 |  |  |  | 10.62 |  | 4.81 | 3 15/16 | 6800 | 400000 | FIXED | 1550 | FLOAT | 711 | 0 | 4365 LB-FT2 | 1856 | 1045 STEEL | 0.14 | 0.60 |  |  | ASTM A572 X-TEN | 5/8 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/8 |  |  | ASTM A1011-HSLAS | 12 | 1856 | 3570 | [9 empty] | ODP | 5750 | 1/2 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 19.847 | 66.000 |  |  |  | 26043 | 329323 | CAST IRON | FALK T10, SIZE 1110T, BORE 3 15/16 NOT INCL. | Direct |  | Required |  | Yes | [9 empty] | 3.9370 | 3.9355 |  | 1.0000 X 0.5000 | 118 1/2 | 25 1/8 | 1125 | SK-19-72 | Yes | Ambient Temp F=70 F; MTL=1045 STEEL; Wheel Gauge=0.105 (12) | Size=6000; Design=1910; Arrangement=7S1; % Width=75.0; Discharge=0; Rotation=CCW; CFM=96453; SP=90; BHP=735.5; RPM=1780; Max Temp F=150; Blade Material=ASTM A572 X-TEN; Blade Gauge=5/8; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/8; Wheel Material=ASTM A1011-HSLAS; Hub=CAST IRON; Coupling=FALK T10, SIZE 1110T, BORE 3 15/16 NOT INCL.; Blades=12; Shaft Dia=6 3/4; Brg Centers=94 11/16; Critical Speed RPM=2485; STB=10.62; STH=4.81; Bearing Size=3 15/16; Bearing Series=6800; Motor Enclosure=ODP; Drive=Direct | Open
416809 | HDX | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | SN416809 | 6000 | 1910 |  |  | 781 | 75.0 | PCT,DISCH TH | CCW |  | 96453 | 39.90 | 735.5 | 1780 | 133 | 150 | 0.0628 | 750.0 | 1800 | 30508 | 6 3/4 | 94 11/16 | 2527 | 109.06 | 19.83 | 82.44 | 10.62 | 960 | 4.81 | 3 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | 1451 | FLOAT | 693 | 0 | 3937 | 1804 | 1045 STEEL | 0.14 | 0.60 |  |  | ASTM A1011-HSLAS | 0.105 (12) | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/2 |  |  | CAST IRON | 12 | 1856 | [10 empty] | ODP | 5750 | 1/2 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 19.847 | 66.000 |  |  |  | 25926 | 315639 | 19-5-54 | FALK T10, SIZE 1110T | SKF 1200 Series Insert & Adaptor Sleeve |  | Required |  | Yes | [9 empty] | 3.9370 | 3.9355 |  | 1.0000 X 0.5000 | 118 1/2 | 25 1/8 | 1082 | SK-19-72 |  | Ambient Temp F=70 | Size=6000; Design=1910; Arrangement=781; % Width=75.0; Discharge=PCT,DISCH TH; Rotation=CCW; CFM=96453; SP=39.90; BHP=735.5; RPM=1780; Max Temp F=150; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Wheel Material=CAST IRON; Hub=19-5-54; Coupling=FALK T10, SIZE 1110T; Blades=12; Shaft Dia=6 3/4; Brg Centers=94 11/16; Critical Speed RPM=2527; BX=82.44; STB=10.62; OH=19.83; STH=4.81; Bearing Size=3 15/16; Bearing Series=LINK BELT SERIES 6800; Motor Enclosure=ODP; Drive=SKF 1200 Series Insert & Adaptor Sleeve | Open
416868 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN-CO#2.pdf |  |  | 416868 | 5414 | 6195 |  |  | 8S | 100.0 | BAU | CCW | 51 9/16 | 65000 | 26.50 | 326.0 | 1770 | 120 | 120 | 0.0674 | 400.0 | 1800 | 24287 | 3 15/16 | 16 | 3787 | 39 5/8 | 11.06 | 23 5/16 | 10 1/8 | 137 | 3.38 | 3 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -405 | FLOAT | 1361 | 0 | 1930 | 1856 | 1045 STEEL | 0.35 | 0.31 |  |  | ASTM A6 XF-100 | 3/16 | ASTM A572 X-TEN | 3/16 | ASTM CQ HRS A36 | 1/2 |  |  |  | 10 | 1856 | 3000 | [7 empty] | 449T |  |  | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 15.920 |  | Included |  | Included | 9786 | 122222 | 19-5-12 | FALK T10 | Direct | Required | Required | Yes | [7 empty] | 3 15/16 |  |  | 3.9370 | 3.9355 | 3.9375 | 1.0000 X 0.5000 |  |  |  | SK-19-72 | Yes | Ambient Temp F=70 | Size=5414; Design=6195; Arrangement=8S; % Width=100.0; Discharge=BAU; Rotation=CCW; CFM=65000; SP=26.50; BHP=326.0; RPM=1770; Max Temp F=120; Effective Wheel Dia=51 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=3/16; Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/2; Hub=19-5-12; Coupling=FALK T10; Blades=10; Shaft Dia=3 15/16; Brg Centers=16; Critical Speed RPM=3787; BX=23 5/16; STB=10 1/8; OH=11.06; STH=3.38; Bearing Size=3 15/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=449T; Drive=Direct | Open
416869 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN PER CO#2.txt |  |  | 416869 | 5414 | 6195 |  |  | 8S | 100.0 | BAU | CCW | 51 9/16 | 80000 | 15.00 | 267.0 | 1652 | 100 | 100 | 0.0698 | 350.0 | 1800 | 24287 | 3 15/16 | 16 | 3785 | 39 5/8 | 11.06 | 23 5/16 | 10 1/8 | 138 | 3.38 | 3 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -403 | FLOAT | 1360 | 0 | 1930 | 1859 | 1045 STEEL | 0.33 | 0.29 | 37 1/8 |  | ASTM A6 XF-100 | 3/16 | ASTM A572 X-TEN | 3/16 | ASTM CQ HRS A36 | 1/2 |  |  |  | 10 | 1859 | 3000 | [7 empty] | 449T |  |  | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 15.920 |  | Included |  | Included | 10552 | 126909 | 19-5-12 | FALK T10 | Direct | Required | Required | Yes | [7 empty] | 3 15/16 |  |  | 3.9370 | 3.9355 | 3.9375 | 1.0000 X 0.5000 |  |  |  | SK-19-72 | Yes | Ambient Temp F=70; Discharge Height (A)=61 3/4; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=40 3/8; Base Width (F)=72 1/2; Shaft Height (H)=66 1/4; Total Vert Height (TV)=105 7/8; Max Right of CL to Hsg (RH)=73 5/8; Max Left of CL to Disch (LH)=48 11/16; Base Flange to CL (D)=96 5/8; Drive End of Shaft to CL (K)=49 11/16; Mtg Flange to CL (LR)=20 13/16 | Size=5414; Design=6195; Arrangement=8S; % Width=100.0; Discharge=BAU; Rotation=CCW; CFM=80000; SP=15.00; BHP=267.0; RPM=1652; Max Temp F=100; Effective Wheel Dia=51 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=3/16; Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/2; Hub=19-5-12; Coupling=FALK T10; Blades=10; Shaft Dia=3 15/16; Brg Centers=16; Critical Speed RPM=3785; BX=23 5/16; STB=10 1/8; OH=11.06; STH=3.38; Bearing Size=3 15/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=37 1/8; Motor Frame=449T; Drive=Direct | Open
416925 | HDX | OK | pdf_vision | QT RUN.pdf |  |  | DESIGN 2300; SIZE 2500; ARR 4 | 2500 | 2300B |  |  | 4S | 100.0 | NOT CW | WHEEL DIA. 25 | 25 | 8000 | 40.00 | 77.3 | 3500 | 70 | 70 | 0.0750 | 150.0 | 3600 | 23562 | 1.30 | [7 empty] | 1.30 | [15 empty] | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.135 (10) |  |  | CAST STEEL |  | 4555 | 5690 | 75 | 138 | 30 | 2.48 | 3.55 |  |  | 445TS |  | TEFC | 2231 | 1/4 GO. JRS | SK-9-236 HI PRESSURE, 19 IN. CENTERS | 0.618 |  | Not included |  | Yes | 2930 | 27339 | HUB 23-5-423 BORE 2 3/8 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 3/8 | [11 empty] | Ambient Temp F=90; Wheel Weight=75 LB; Thrust=138 LB; Outlet=6 3/4 IN. X 13 3/16 IN.; Base=445TS FR MOTOR | Size=2500; Design=2300B; Arrangement=4S; % Width=100.0; Discharge=NOT CW; Rotation=WHEEL DIA. 25; CFM=8000; SP=40.00; BHP=77.3; RPM=3500; Max Temp F=70; Effective Wheel Dia=25; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.135 (10); Wheel Material=CAST STEEL; Hub=HUB 23-5-423 BORE 2 3/8; Shaft Dia=1.30; STH=1.30; Motor Frame=445TS; Motor Enclosure=TEFC; Drive=Motor mounted | Open
416934 | GENERAL LINE | OK | cbc_qt_run_text | quote run.docx |  |  | 416934 | 22-1/4 | B10 | 4 |  | 8S | 90.0 | TH | CCW |  | 16000 | 21.00 | 78.3 | 3555 | 70 | 70 | 0.0750 | 100.0 | 3600 | 22627 | 2 3/16 | 14 | 4800 | 34 1/8 | 8.25 | 13 9/16 | 11 | 36 | 2.27 | 2 3/16 | LINK BELT SERIES 300 | 400000 | FIXED | -11 | FLOAT | 147 | 0 | 39 | 3650 | 1045 STEEL | 0.23 | 0.22 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 12 | 4303 | 5780 | [7 empty] | 405TS |  | TEFC | 1575 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 2.851 | [6 empty] | 19-5-26 | FALK T10 | Direct |  |  |  |  | Yes | [5 empty] | 2 3/16 | [10 empty] | Yes | Ambient Temp F=90 | Size=22-1/4; Design=B10; Arrangement=8S; % Width=90.0; Discharge=TH; Rotation=CCW; Class=4; CFM=16000; SP=21.00; BHP=78.3; RPM=3555; Max Temp F=70; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=19-5-26; Coupling=FALK T10; Blades=12; Shaft Dia=2 3/16; Brg Centers=14; Critical Speed RPM=4800; BX=13 9/16; STB=11; OH=8.25; STH=2.27; Bearing Size=2 3/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=405TS; Motor Enclosure=TEFC; Drive=Direct | Open
416937 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 416937 | 22.250 | 6195 |  |  | 4S | 100.0 | UB | CW | 21 1/8 | 11000 | 15.00 | 33.8 | 3550 | 70 | 70 | 0.0750 | 40.0 | 3600 | 19922 | [8 empty] | 1.62 | [15 empty] | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) |  |  |  | 10 | 3793 | 4740 | 53 | 73 | 21 | 3.19 | 4.62 |  |  | 324TS |  |  | 550 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 2.709 |  | Not included |  | Yes |  |  | 19-5-1055 |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q2 BUSHING 1 7/8 | [9 empty] | Ambient Temp F=70 | Size=22.250; Design=6195; Arrangement=4S; % Width=100.0; Discharge=UB; Rotation=CW; CFM=11000; SP=15.00; BHP=33.8; RPM=3550; Max Temp F=70; Effective Wheel Dia=21 1/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.075 (14); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.105 (12); Hub=19-5-1055; Blades=10; STH=1.62; Motor Frame=324TS; Drive=Motor mounted | Open
416941 | GENERAL LINE | OK | cbc_qt_run_text | QT Run.txt |  |  | 416941 | 22-1/4 | B10 | 4 |  | 9H | 60.0 | TH | CW |  | 10000 | 10.00 | 40.0 | 2814 | 70 | 70 | 0.0750 | 40.0 | 2814 | 17687 | 2 7/16 | 12 | 7351 | 30 3/4 | 7.49 | 12 7/16 | 9 7/8 |  | 2.27 | 2 7/16 | LINK BELT SERIES 6800 | 400000 | FIXED | 774 | FIXED | 208 | 69 | 35 | 3400 | 1045 STEEL | 0.09 | 0.28 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 12 | 5270 | [6 empty] | 5.4 | 3.0 | 365T | W |  | 920 | 10 GA C.Q. HRS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 2.587 | [6 empty] | 19-5-26 |  | Belt |  |  |  |  | Yes | [5 empty] | 2 7/16 | [10 empty] | Yes | Ambient Temp F=90 | Size=22-1/4; Design=B10; Arrangement=9H; % Width=60.0; Discharge=TH; Rotation=CW; Class=4; CFM=10000; SP=10.00; BHP=40.0; RPM=2814; Max Temp F=70; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=19-5-26; Blades=12; Shaft Dia=2 7/16; Brg Centers=12; Critical Speed RPM=7351; BX=12 7/16; STB=9 7/8; OH=7.49; STH=2.27; Bearing Size=2 7/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=365T; Motor Position=W; Drive=Belt | Open
416987 | GENERAL LINE | OK | cbc_qt_run_text | 339-25-368 - Revised QT Run.txt |  |  | 416987 | 22 | A10 |  |  | 4S | 115.0 | TH | CW |  | 7000 | 5.00 | 10.0 | 1750 | 150 | 150 | 0.0620 | 10.0 | 1750 | 10999 | [8 empty] | 2.27 | [15 empty] | ASTM A1008 HSLAS | 0.048 (18) | ASTM A1011 CS | 0.060 (16) | ASTM A1011 CS | 0.105 (12) |  |  |  | 8 | 2548 | 7220 | 60 | 26 | 21 | 4.18 | 4.52 |  |  | 215T |  |  | 200 | 10 GA C.Q. HRS | SK-9-236 LOW PRESSURE, 36 IN. CENTERS | 3.077 |  | Not included |  |  |  |  | 19-5-26 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 1 3/8 | [11 empty] | Ambient Temp F=90 | Size=22; Design=A10; Arrangement=4S; % Width=115.0; Discharge=TH; Rotation=CW; CFM=7000; SP=5.00; BHP=10.0; RPM=1750; Max Temp F=150; Blade Material=ASTM A1008 HSLAS; Blade Gauge=0.048 (18); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.060 (16); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.105 (12); Hub=19-5-26; Blades=8; STH=2.27; Motor Frame=215T; Drive=Motor mounted | Open
417023 | HDX | OK | cbc_qt_run_text | QT RUN-FEA UPDATE.pdf |  |  | 417023 | 4900 | 5500 |  |  | 7S1 | 100.0 | TH | CW | 49 | 30605 | 28.32 | 174.2 | 1780 | 129 | 130 | 0.0652 | 200.0 | 1800 | 23091 | 3 3/16 | 49 | 2791 |  |  |  | 7.38 |  | 2.00 | 2 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | 485 | FLOAT | 159 | 0 | 984 | 1993 | 4140 STEEL | 0.33 | 0.38 |  |  | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 3/8 |  |  |  | 16 | 2437 | [8 empty] | 447T |  |  | 2850 | 1/4 A572 X-TEN | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 6.293 |  | Included | 3.00 |  | 8476 | 212697 | 49-5-145- |  | Direct |  |  |  | Yes | Yes | [5 empty] | 3 3/16 |  |  | 2.9370 | 2.9355 |  | 0.7500 X 0.3750 | 66 3/4 | 21 1/16 | 1125 | SK-55-11 | Yes |  | Size=4900; Design=5500; Arrangement=7S1; % Width=100.0; Discharge=TH; Rotation=CW; CFM=30605; SP=28.32; BHP=174.2; RPM=1780; Max Temp F=130; Effective Wheel Dia=49; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Hub=49-5-145-; Blades=16; Shaft Dia=3 3/16; Brg Centers=49; Critical Speed RPM=2791; STB=7.38; STH=2.00; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=447T; Drive=Direct | Open
417129 | GENERAL LINE | OK | pdf_vision | QT RUN_GMH.pdf |  |  | SN417129 | 3000 | 6195 |  |  | 4S | 80.0 | ROT CCW | CCW | 28 1/2 | 25166 | 14.00 | 99.0 | 3570 | 105 | 130 | 0.0686 | 150.0 | 3600 | 26861 | [8 empty] | 1.94 |  | Q2 BUSHING | [13 empty] | ASTM A6 XF-100 | 1/4 | ASTM A6 XF-100 | 3/16 | ASTM A572 X-TEN | 3/8 |  |  | CAST STEEL | 10 | 4428 | 9020 | 185 | 243 | 153 | 3.56 | 4.94 |  |  |  |  | TEFC | 2187 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS |  |  | Not included |  | Included |  |  | BORE 2 3/8 |  | Motor mounted | Required |  | Yes |  | Yes | [5 empty] | 2 3/8 | [11 empty] | Ambient Temp F=90; Wheel Weight=185 LB; Bearing Quantity=3 SET SCREWS OR TAPERLOCK BUSHING; Resonance CPM=9020; Thrust=243 LB; WR2=153 LB-FT2; Outlet N x A=19; Outlet Dimension=34 1/8 IN; Base=444/5TS FR MOTOR; Outlet Damper Torque=675 IN-LB AT PEAK SP STD AIR; Damper Frame=A36; Damper Frame Thickness=1/4; Misc Material=1104; Good For Days=60 | Size=3000; Design=6195; Arrangement=4S; % Width=80.0; Discharge=ROT CCW; Rotation=CCW; CFM=25166; SP=14.00; BHP=99.0; RPM=3570; Max Temp F=130; Effective Wheel Dia=28 1/2; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=3/16; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Wheel Material=CAST STEEL; Hub=BORE 2 3/8; Blades=10; STH=1.94; Bearing Series=Q2 BUSHING; Motor Enclosure=TEFC; Drive=Motor mounted | Open
417129 | GENERAL LINE | OK | pdf_vision | QT RUN-5-6-2025.pdf |  |  | SN417129 | 3000 | DESIGN 6195 |  |  | 4S | 80.0 | ARB 4S, DISCH UB, ROT CCW | CCW | 28 1/2 | 25166 | 14.00 | 99.0 | 3570 | 105 | 130 | 0.0686 | 150.0 | 3600 | 26861 | [8 empty] | 1.94 | [15 empty] | ASTM A6 XF-100 | 1/4 | ASTM A6 XF-100 | 3/16 | ASTM A572 X-TEN | 3/8 |  |  | CAST STEEL | 10 | 4428 | 9020 | 185 | 243 | 153 | 3.56 | 4.94 |  |  |  |  | TEFC |  | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS |  |  | Not included |  | Included |  |  | BORE 2 3/8 |  | Motor mounted | Required |  | Yes |  | Yes | [5 empty] | 2 3/8 | [11 empty] | Ambient Temp F=90; Number of Blades=10; Wheel Weight=185; Thrust=243; Outlet N x A=19 IN. x 34 1/8 IN.; Base=444/5TS FR MOTOR; Outlet Damper Torque=875 IN-LB AT PEAK SP STD AIR; Pan Outlet Area=4.503 FT2; Evase Area=5.033 FT2 | Size=3000; Design=DESIGN 6195; Arrangement=4S; % Width=80.0; Discharge=ARB 4S, DISCH UB, ROT CCW; Rotation=CCW; CFM=25166; SP=14.00; BHP=99.0; RPM=3570; Max Temp F=130; Effective Wheel Dia=28 1/2; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=3/16; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Wheel Material=CAST STEEL; Hub=BORE 2 3/8; Blades=10; STH=1.94; Motor Enclosure=TEFC; Drive=Motor mounted | Open
417152 | HDX | OK | cbc_qt_run_text | QUOTE RUN-CO#1.pdf |  |  | 417152 | 6000 | 5500 |  |  | 7S1 | 100.0 | TH | CCW | 62 1/2 | 61739 | 42.30 | 513.0 | 1766 | 165 | 180 | 0.0598 | 600.0 | 1800 | 29452 | 4 7/16 | 63 | 2742 |  |  |  | 10.50 |  | 2.38 | 3 7/16 | LINK BELT SERIES 6800 | 179136 | FIXED | 767 | FLOAT | 291 | 0 | 2027 | 1936 | 1045 STEEL | 0.37 | 0.76 |  |  | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A572 X-TEN | 5/16 |  |  |  | 16 | 1936 | [10 empty] | ODP | 5137 | 5/16 C.Q. HRS | SK-9-236 HI PRESSURE, 18 IN. CENTERS | 9.421 |  | Included | 3.00 |  | 17227 | 200244 | 49-5-146- |  | Direct |  |  |  | Yes | [6 empty] | 4 7/16 |  |  | 3.4370 | 3.4355 |  | 0.8750 X 0.4375 | 81 3/4 | 25 13/16 | 1125 | SK-55-11 | Yes | Ambient Temp F=70 | Size=6000; Design=5500; Arrangement=7S1; % Width=100.0; Discharge=TH; Rotation=CCW; CFM=61739; SP=42.30; BHP=513.0; RPM=1766; Max Temp F=180; Effective Wheel Dia=62 1/2; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 ( 7); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=49-5-146-; Blades=16; Shaft Dia=4 7/16; Brg Centers=63; Critical Speed RPM=2742; STB=10.50; STH=2.38; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Motor Enclosure=ODP; Drive=Direct | Open
417321 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 417321 | 3000 | 5800 |  |  | 4S | 100.0 | TAU | CCW | 31 | 10000 | 47.00 | 101.6 | 3570 | 100 | 100 | 0.0653 | 150.0 | 3600 | 29217 | 1 15/16 | 12 | 5626 | 25 9/16 | 5.91 | 9 7/16 | 6 |  | 1.38 | 1 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -16 | FLOAT | 158 | 0 | 71 | 4146 | 1045 STEEL | 0.74 | 0.47 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) |  |  |  | 10 | 4146 |  | 103 | 166 | 71 | 2.47 | 3.62 |  |  | 445TS |  |  | 1785 | 1/4 A572 X-TEN | SK-9-236 HI PRESSURE, 18 IN. CENTERS | 1.172 |  | Not included |  | Included | 2992 | 41790 | 23-5-423 | FALK G20 | Motor mounted | Required | Required |  | Yes | Yes | [5 empty] | 2 3/8 |  |  | 1.9370 | 1.9360 | 1.9375 | 0.5000 X 0.2500 |  |  |  |  | Yes |  | Size=3000; Design=5800; Arrangement=4S; % Width=100.0; Discharge=TAU; Rotation=CCW; CFM=10000; SP=47.00; BHP=101.6; RPM=3570; Max Temp F=100; Effective Wheel Dia=31; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.135 (10); Hub=23-5-423; Coupling=FALK G20; Blades=10; Shaft Dia=1 15/16; Brg Centers=12; Critical Speed RPM=5626; BX=9 7/16; STB=6; OH=5.91; STH=1.38; Bearing Size=1 15/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=445TS; Drive=Motor mounted | Open
417362 | GENERAL LINE | OK | cbc_qt_run_text | qt run.txt |  |  | 417362 | 19 | 16A | 3 |  | 9H | 100.0 | UB | CW | 33 | 5865 | 39.00 | 60.0 | 2416 | 70 | 70 | 0.0750 | 60.0 | 2447 |  | 2 11/16 | 12 | 3725 | 41 1/8 | 12.88 | 12 7/8 | 13 9/16 |  |  | 2 11/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 1319 | FIXED | 471 | 0 | 75 | 2535 | A240 316 SS | 0.18 | 0.61 | [10 empty] | A240 316L SS | 6 | 2535 | [6 empty] | 6.3 | 3.7 | [15 empty] | Belt |  |  | Yes |  | Yes | [5 empty] | 2 11/16 | [11 empty] | Ambient Temp F=70 | Size=19; Design=16A; Arrangement=9H; % Width=100.0; Discharge=UB; Rotation=CW; Class=3; CFM=5865; SP=39.00; BHP=60.0; RPM=2416; Max Temp F=70; Effective Wheel Dia=33; Wheel Material=A240 316L SS; Blades=6; Shaft Dia=2 11/16; Brg Centers=12; Critical Speed RPM=3725; BX=12 7/8; STB=13 9/16; OH=12.88; Bearing Size=2 11/16; Bearing Series=LINK BELT SERIES 6800; Drive=Belt | Open
417385 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.txt |  |  | 417385 | 4014 | 1904 |  | PACKAGED FORCED DRAFT FAN | 4S1 | 55.0 | DB | CW | 44 1/4 | 17648 | 20.12 | 77.5 | 1770 | 105 | 105 | 0.0685 | 100.0 | 1800 | 20864 | [8 empty] | 2.50 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 5/16 |  |  |  | 10 | 2271 | 2840 | 284 | 292 | 451 | 3.79 | 7.25 |  |  | 404T |  | TEFC | 1431 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 7.437 |  | Not included |  |  |  |  | 19-5-16 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 7/8 | [6 empty] | 73 | 15 9/16 | 1 | SK-19-72 |  | Ambient Temp F=90 | Size=4014; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S1; % Width=55.0; Discharge=DB; Rotation=CW; CFM=17648; SP=20.12; BHP=77.5; RPM=1770; Max Temp F=105; Effective Wheel Dia=44 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=5/16; Hub=19-5-16; Blades=10; STH=2.50; Motor Frame=404T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
417386 | HD-PFD-IAF | OK | cbc_qt_run_text | QUOTE RUN 4-22-25.txt |  |  | 417385 | 4014 | 1904 |  | PACKAGED FORCED DRAFT FAN | 4S1 | 55.0 | DB | CW | 44 1/4 | 17648 | 20.12 | 77.5 | 1770 | 105 | 105 | 0.0685 | 100.0 | 1800 | 20864 | [8 empty] | 2.50 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 5/16 |  |  |  | 10 | 2271 | 2840 | 284 | 292 | 451 | 3.79 | 7.25 |  |  | 404T |  | TEFC | 1431 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 7.437 |  | Not included |  |  |  |  | 19-5-16 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 7/8 | [6 empty] | 73 | 15 9/16 | 1 | SK-19-72 |  | Ambient Temp F=90 | Size=4014; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S1; % Width=55.0; Discharge=DB; Rotation=CW; CFM=17648; SP=20.12; BHP=77.5; RPM=1770; Max Temp F=105; Effective Wheel Dia=44 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=5/16; Hub=19-5-16; Blades=10; STH=2.50; Motor Frame=404T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
417395 | HD-PFD-IAF | CHECK VISION | pdf_vision | QUOTE RUN.pdf |  |  | SN#417395 | 4412 | 5800 |  |  | 48 | 100.0 | TH | RCW | 42 1/2 | 14000 | 22.00 | 67.0 | 1780 | 86 | 86 | 0.0673 | 75.0 | 1800 | 20028 | 1 15/16 | 14 | 3454 | [5 empty] | 2.06 | 1 15/16 | LINK BELT SERIES 300 | [13 empty] | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 (7) |  |  | CAST STEEL | 10 | 2893 |  | 184 | 167 | 270 | 3.68 | 4.26 |  |  | 365T |  |  | 920 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 2.591 |  | Not included |  | Yes | 2983 | 51463 | HUB 2 3/8 BORE | FALK G20, SIZE 1020G, BORE 1.938 | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 3/8 | [11 empty] | Ambient Temp F=70 F | Size=4412; Design=5800; Arrangement=48; % Width=100.0; Discharge=TH; Rotation=RCW; CFM=14000; SP=22.00; BHP=67.0; RPM=1780; Max Temp F=86; Effective Wheel Dia=42 1/2; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 (7); Wheel Material=CAST STEEL; Hub=HUB 2 3/8 BORE; Coupling=FALK G20, SIZE 1020G, BORE 1.938; Blades=10; Shaft Dia=1 15/16; Brg Centers=14; Critical Speed RPM=3454; STH=2.06; Bearing Size=1 15/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=365T; Drive=Motor mounted | Open
417445 | GENERAL LINE | OK | cbc_qt_run_text | 417445 QT RUN UPDATE PER FEA - CO#3.docx |  | sheave | 417445 | 6600 | 6105 |  |  | 9H | 90.0 | BAU | CW | 69 5/16 | 83087 | 27.00 | 250.0 | 1224 | 70 | 70 | 0.0741 | 250.0 | 1250 | 22678 | 4 15/16 | 22 | 3033 | 60 9/16 | 12.13 | 27 | 23 1/2 |  | 3.69 | 4 15/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 5601 | FIXED | 1842 | 982 | 4085 | 1269 | 1045 STEEL | 0.21 | 0.57 | 43 3/4 | 42 | GA. ASTM A1011-HSLAS | 7 | GA. ASTM A1011-HSLAS | 7 | ASTM A572 X-TEN | 1/2 |  |  |  | 10 | 1269 | 1640 | [7 empty] | 449T | W |  | 2600 | 3/8 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 22.805 |  | Included |  | Yes | 14169 | 227639 | 19-5-218 |  | Belt | Required |  | Yes | Yes | Yes | [5 empty] | 4 11/16 | [10 empty] | Yes | Ambient Temp F=70; Discharge Height (A)=75 1/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=3; Discharge Flange to CL (E)=49; Unitary Base to CL (RB)=95 11/16; Motor CL to Fan CL (RM)=73 13/16; Shaft Height (H)=78 9/16; Total Vert Height (TV)=126 5/8; Max Right of CL to Hsg (RH)=59 1/16; Max Left of CL to Disch (LH)=89 13/16; Mounting Channel (MA)=2 1/4; Base Flange to CL (D)=55 7/16; Drive End of Shaft to CL (K)=72 1/2; Mtg Flange to CL (LR)=24 1/8 | Size=6600; Design=6105; Arrangement=9H; % Width=90.0; Discharge=BAU; Rotation=CW; CFM=83087; SP=27.00; BHP=250.0; RPM=1224; Max Temp F=70; Effective Wheel Dia=69 5/16; Blade Material=GA. ASTM A1011-HSLAS; Blade Gauge=7; Sideplate Material=GA. ASTM A1011-HSLAS; Sideplate Gauge=7; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Hub=19-5-218; Blades=10; Shaft Dia=4 15/16; Brg Centers=22; Critical Speed RPM=3033; BX=27; STB=23 1/2; OH=12.13; STH=3.69; Bearing Size=4 15/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=43 3/4; Base to CL (F)=42; Motor Frame=449T; Motor Position=W; Drive=Belt | Open
417594 | HDX | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 417594 | 4900 | 1904 |  |  | 7S1 | 75.0 | TH | CW | 53 7/8 | 46347 | 29.30 | 268.0 | 1785 | 130 | 150 | 0.0633 | 300.0 | 1800 | 25400 | 3 11/16 | 59 | 2636 |  |  |  | 9.38 |  | 2.94 | 3 3/16 | LINK BELT SERIES 6800 | 148607 | FIXED | 726 | FLOAT | 205 | 0 | 1683 | 1882 | 1045 STEEL | 0.32 | 0.45 |  |  | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A572 X-TEN | 1/2 |  |  |  | 10 | 1974 | 2760 | [7 empty] | 449T |  |  | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 11.870 |  | Included |  |  | 9587 | 125001 | 19-5-219 | FALK T10 | Direct |  |  |  | Yes | [9 empty] | 3.1870 | 3.1855 |  | 0.7500 X 0.3750 | 88 1/4 | 18 3/4 | 1125 | SK-19-72 | Yes | Ambient Temp F=10 | Size=4900; Design=1904; Arrangement=7S1; % Width=75.0; Discharge=TH; Rotation=CW; CFM=46347; SP=29.30; BHP=268.0; RPM=1785; Max Temp F=150; Effective Wheel Dia=53 7/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 ( 7); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Hub=19-5-219; Coupling=FALK T10; Blades=10; Shaft Dia=3 11/16; Brg Centers=59; Critical Speed RPM=2636; STB=9.38; STH=2.94; Bearing Size=3 3/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=449T; Drive=Direct | Open
417653 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 417653 | 3000 | 5500 |  |  | 4S1 | 100.0 | UB | CCW | 32 | 16580 | 40.25 | 134.0 | 3589 | 180 | 180 | 0.0533 | 150.0 | 3600 | 30159 | [8 empty] | 1.25 | [15 empty] | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) |  |  |  | 16 | 3911 |  | 110 | 226 | 81 | 2.40 | 3.50 |  |  | 445TS |  |  | 1785 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 18 IN. CENTERS | 2.358 |  | Not included |  |  | 3351 | 47908 | 23-5-423 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 3/8 | [6 empty] | 41 | 12 7/8 | 1 |  |  | Ambient Temp F=70 | Size=3000; Design=5500; Arrangement=4S1; % Width=100.0; Discharge=UB; Rotation=CCW; CFM=16580; SP=40.25; BHP=134.0; RPM=3589; Max Temp F=180; Effective Wheel Dia=32; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.135 (10); Hub=23-5-423; Blades=16; STH=1.25; Motor Frame=445TS; Drive=Motor mounted | Open
417810 | HDX | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 417810 | 3300 | 4806 |  |  | 1S | 100.0 | TAD | CCW | 35 | 30014 | 24.10 | 164.0 | 2361 | 113 | 113 | 0.0653 | 250.0 | 2361 | 21652 | 3 7/16 | 22 | 5474 | 46 1/4 | 8.29 | 13 15/16 | 13 15/16 |  | 1.36 | 3 7/16 | LINK BELT SERIES 6800 | 304651 | FLOAT | 2949 | FIXED | 663 | 93 | 290 | 2800 | 1045 STEEL | 0.28 | 0.90 |  |  | ASTM A572 X-TEN | 5/16 | ASTM A572 X-TEN | 5/16 | ASTM CQ HRS A36 | 3/8 |  |  |  | 12 | 2974 | 4780 | [5 empty] | 6.5 | 5.8 |  |  |  |  | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 4.012 |  | Included |  | Included | 2391 | 73134 | 19-5-11 |  | Belt |  |  | Yes | Yes | Yes | [5 empty] | 3 3/16 | [10 empty] | Yes | Ambient Temp F=90 | Size=3300; Design=4806; Arrangement=1S; % Width=100.0; Discharge=TAD; Rotation=CCW; CFM=30014; SP=24.10; BHP=164.0; RPM=2361; Max Temp F=113; Effective Wheel Dia=35; Blade Material=ASTM A572 X-TEN; Blade Gauge=5/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=5/16; Backplate Material=ASTM CQ HRS A36; Backplate Gauge=3/8; Hub=19-5-11; Blades=12; Shaft Dia=3 7/16; Brg Centers=22; Critical Speed RPM=5474; BX=13 15/16; STB=13 15/16; OH=8.29; STH=1.36; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Drive=Belt | Open
417813 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 417813 | 3612 | 6195 |  |  | 9H | 100.0 | UB | CW | 34 11/16 | 28000 | 14.00 | 81.7 | 2061 | 70 | 70 | 0.0750 | 100.0 | 2086 | 18937 | 2 15/16 | 12 | 4502 | 34 5/8 | 9.07 | 16 1/2 | 12 | 67 | 2.25 | 2 15/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 1577 | FIXED | 485 | 179 | 397 | 2918 | 1045 STEEL | 0.20 | 0.47 | 25 | 25 1/2 | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM CQ HRS A36 | 3/8 |  |  |  | 10 | 2918 | 5160 | [5 empty] | 7.4 | 3.3 | 405T | W |  | 1260 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 7.216 |  | Included |  | Yes | 3640 | 63584 | 19-5-16 |  | Belt |  |  | Yes |  | Yes | [5 empty] | 2 15/16 | [10 empty] | Yes | Discharge Height (A)=41 9/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=27 3/4; Unitary Base to CL (RB)=72 3/16; Motor CL to Fan CL (RM)=50 13/16; Shaft Height (H)=39 7/16; Total Vert Height (TV)=67 3/16; Max Right of CL to Hsg (RH)=29 7/8; Max Left of CL to Disch (LH)=43 9/16; Mounting Channel (MA)=3; Base Flange to CL (D)=33 3/4; Drive End of Shaft to CL (K)=40 1/2; Mtg Flange to CL (LR)=15 1/2 | Size=3612; Design=6195; Arrangement=9H; % Width=100.0; Discharge=UB; Rotation=CW; CFM=28000; SP=14.00; BHP=81.7; RPM=2061; Max Temp F=70; Effective Wheel Dia=34 11/16; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM CQ HRS A36; Backplate Gauge=3/8; Hub=19-5-16; Blades=10; Shaft Dia=2 15/16; Brg Centers=12; Critical Speed RPM=4502; BX=16 1/2; STB=12; OH=9.07; STH=2.25; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=25; Base to CL (F)=25 1/2; Motor Frame=405T; Motor Position=W; Drive=Belt | Open
417821 | GENERAL LINE | OK | cbc_qt_run_text | D51 Plenum BT24-0228 Quote Run REV 2.txt |  |  | 417821 | 402 | 51A | 1 |  | 1 |  |  |  |  | 36716 | 12.00 | 99.4 | 2073 |  |  |  |  | 2200 | 21369 | 3 7/16 | 30 | 3823 | 57 11/16 | 11.58 | 20 13/16 | 14 1/8 | 152 | 3.44 | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | -1256 | FIXED | 659 | 289 | 225 | 2200 | 1045 STEEL | 0.16 | 0.33 |  |  | ASTM A1008 HSLAS | 0.060 (16) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011 CS | 0.179 ( 7) |  |  |  | 8 | 2393 | 4700 | [5 empty] | 9.2 | 3.4 | [13 empty] | 19-5-16 |  | Belt | Required |  |  |  | Yes | [5 empty] | 3 7/16 | [11 empty] | Ambient Temp F=18 | Size=402; Design=51A; Arrangement=1; Class=1; CFM=36716; SP=12.00; BHP=99.4; RPM=2073; Blade Material=ASTM A1008 HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.179 ( 7); Hub=19-5-16; Blades=8; Shaft Dia=3 7/16; Brg Centers=30; Critical Speed RPM=3823; BX=20 13/16; STB=14 1/8; OH=11.58; STH=3.44; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Drive=Belt | Open
417821 | GENERAL LINE | OK | cbc_qt_run_text | 417821 QT RUN D10 36.5 115pct - 6in OH - IT02.txt |  |  | 417821 | 36 | A10 |  |  | 1S | 115.0 | BAU | CW |  | 36716 | 12.00 | 97.0 | 1890 | 344 | 444 | 0.0495 | 100.0 | 1890 | 19487 | 3 7/16 | 30 | 3636 | 57 | 11.58 | 21 | 14 1/8 | 150 | 3.44 | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | -1559 | FIXED | 769 | 217 | 281 | 2077 | 1045 STEEL | 0.18 | 0.41 |  |  | ASTM A1008 HSLAS | 0.060 (16) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011 CS | 0.179 ( 7) |  |  |  | 12 | 2077 | 4280 | [5 empty] | 8.1 | 3.4 |  |  |  |  | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 8.319 |  |  |  |  | 2508 | 52144 |  |  | Belt |  |  |  |  | Yes | [5 empty] | 3 7/16 | [10 empty] | Yes | Ambient Temp F=18 | Size=36; Design=A10; Arrangement=1S; % Width=115.0; Discharge=BAU; Rotation=CW; CFM=36716; SP=12.00; BHP=97.0; RPM=1890; Max Temp F=444; Blade Material=ASTM A1008 HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.179 ( 7); Blades=12; Shaft Dia=3 7/16; Brg Centers=30; Critical Speed RPM=3636; BX=21; STB=14 1/8; OH=11.58; STH=3.44; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Drive=Belt | Open
417843 | HDX | OK | cbc_qt_run_text | QT RUN-UPDATE PER FEA.pdf |  |  | 417843 | 2412 | 1904 |  |  | 8S | 100.0 | UB | CW | 26 15/16 | 8732 | 4.50 | 9.9 | 1760 | 100 | 125 | 0.0690 | 15.0 | 1800 | 12700 | 1 11/16 | 12 | 3543 | 24 9/16 | 6.87 | 11 3/4 | 4 7/8 |  | 1.62 | 1 11/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -50 | FLOAT | 182 | 0 | 67 | 2708 | 1045 STEEL | 0.42 | 0.15 |  |  | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 10 | 2708 | 3390 | [7 empty] | 254T |  |  | 230 |  | SK-9-236 MED PRESSURE, 30 IN. CENTERS | 3.274 |  | Included |  | Included |  |  | 19-5-26 |  | Direct |  |  |  | Yes | Yes | [5 empty] | 1 7/16 |  |  | 1.6870 | 1.6860 | 1.6875 | 0.3750 X 0.1875 |  |  |  |  | Yes | Ambient Temp F=70 | Size=2412; Design=1904; Arrangement=8S; % Width=100.0; Discharge=UB; Rotation=CW; CFM=8732; SP=4.50; BHP=9.9; RPM=1760; Max Temp F=125; Effective Wheel Dia=26 15/16; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=19-5-26; Blades=10; Shaft Dia=1 11/16; Brg Centers=12; Critical Speed RPM=3543; BX=11 3/4; STB=4 7/8; OH=6.87; STH=1.62; Bearing Size=1 11/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=254T; Drive=Direct | Open
417845 | GENERAL LINE | OK | cbc_qt_run_text | QUOTE RUN.txt |  |  | 417845 | 600 | 51A | 3 |  | 8 | 80.0 |  |  |  | 50000 | 17.00 | 160.1 | 1200 |  |  |  |  | 1215 | 18378 | 3 3/16 | 18 | 2510 | 42 1/2 | 12.14 | 26 3/4 | 9 1/4 | 96 | 4.88 | 3 3/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -298 | FLOAT | 977 | 0 | 1382 | 1215 | 1045 STEEL | 0.48 | 0.42 |  |  | ASTM A1011 CS | 0.075 (14) | ASTM A1011 CS | 0.105 (12) | ASTM CQ HRS A36 | 5/16 |  |  |  | 8 | 1215 | 4040 | [7 empty] | 449T |  | ODP | 2600 | [9 empty] | 10-5-414 | FALK T10 | Direct | Required |  |  |  | Yes | [5 empty] | 3 3/16 | [11 empty] | Ambient Temp F=70 | Size=600; Design=51A; Arrangement=8; % Width=80.0; Class=3; CFM=50000; SP=17.00; BHP=160.1; RPM=1200; Blade Material=ASTM A1011 CS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=5/16; Hub=10-5-414; Coupling=FALK T10; Blades=8; Shaft Dia=3 3/16; Brg Centers=18; Critical Speed RPM=2510; BX=26 3/4; STB=9 1/4; OH=12.14; STH=4.88; Bearing Size=3 3/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=449T; Motor Enclosure=ODP; Drive=Direct | Open
418170 | HDX | OK | cbc_qt_run_text | QT RUN (NOT FOR CONSTRUCTION).txt |  |  | 418170 | 7300 | 1910 |  |  | 3S1 | 90.0 | TAU | CW |  | 100000 | 16.00 | 298.7 | 900 | 150 | 150 | 0.0674 | 400.0 | 900 | 18559 | 5 1/2 | 108 | 1212 |  |  |  | 12.38 |  | 6.25 | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FIXED | 1686 | FLOAT | 740 | 0 | 7703 | 969 | 1045 STEEL | 0.33 | 0.95 |  |  | ASTM A606 CORTEN | 0.105 (12) | ASTM A606 CORTEN | 0.179 ( 7) | ASTM A242 CORTEN | 3/8 |  |  |  | 12 | 1174 | 1480 | [11 empty] | 1/4 C.Q. HRS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 30.615 | [6 empty] | 19-5-36 | FALK G20 | Direct | [17 empty] | 131 1/2 | 27 7/8 | 270 |  | Yes | Ambient Temp F=90 | Size=7300; Design=1910; Arrangement=3S1; % Width=90.0; Discharge=TAU; Rotation=CW; CFM=100000; SP=16.00; BHP=298.7; RPM=900; Max Temp F=150; Blade Material=ASTM A606 CORTEN; Blade Gauge=0.105 (12); Sideplate Material=ASTM A606 CORTEN; Sideplate Gauge=0.179 ( 7); Backplate Material=ASTM A242 CORTEN; Backplate Gauge=3/8; Hub=19-5-36; Coupling=FALK G20; Blades=12; Shaft Dia=5 1/2; Brg Centers=108; Critical Speed RPM=1212; STB=12.38; STH=6.25; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Drive=Direct | Open
418260 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 418260 | 5414 | 6195 |  |  | 9H | 100.0 | BAU | CW | 51 9/16 | 60000 | 14.00 | 173.3 | 1367 | 70 | 70 | 0.0750 | 200.0 | 1482 | 19996 | 3 15/16 | 16 | 3302 | 42 3/8 | 12.32 | 23 5/16 | 12 7/8 |  | 3.38 | 3 15/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 3137 | FIXED | 1007 | 440 | 2090 | 1784 | 1045 STEEL | 0.26 | 0.48 | 37 1/8 | 36 1/4 | ASTM A6 XF-100 | 5/16 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 3/8 |  |  |  | 10 | 1784 | 2570 | [5 empty] | 11.2 | 4.4 | 447T | W |  | 2280 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 15.920 |  |  |  | Included | 8178 | 111091 | 19-5-17 |  | Belt |  |  | Yes |  | Yes | [5 empty] | 3 15/16 | [10 empty] | Yes | Ambient Temp F=70; Discharge Height (A)=61 3/4; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=40 3/8; Unitary Base to CL (RB)=87 1/2; Motor CL to Fan CL (RM)=65 5/8; Shaft Height (H)=66 1/4; Total Vert Height (TV)=105 7/8; Max Right of CL to Hsg (RH)=48 11/16; Max Left of CL to Disch (LH)=73 5/8; Mounting Channel (MA)=2 1/4; Base Flange to CL (D)=45 3/16; Drive End of Shaft to CL (K)=52 3/16; Mtg Flange to CL (LR)=20 13/16 | Size=5414; Design=6195; Arrangement=9H; % Width=100.0; Discharge=BAU; Rotation=CW; CFM=60000; SP=14.00; BHP=173.3; RPM=1367; Max Temp F=70; Effective Wheel Dia=51 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=5/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Hub=19-5-17; Blades=10; Shaft Dia=3 15/16; Brg Centers=16; Critical Speed RPM=3302; BX=23 5/16; STB=12 7/8; OH=12.32; STH=3.38; Bearing Size=3 15/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=37 1/8; Base to CL (F)=36 1/4; Motor Frame=447T; Motor Position=W; Drive=Belt | Open
418281 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 418281 | 4014 | 5800 |  |  | 8S | 100.0 | UB | CW | 41 3/4 | 10000 | 24.00 | 49.5 | 1780 | 120 | 120 | 0.0661 | 75.0 | 1800 | 19674 | 2 3/16 | 14 | 4177 | 29 3/16 | 7.21 | 11 7/8 | 6 3/4 | 31 | 2.00 | 2 3/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -53 | FLOAT | 281 | 0 | 250 | 3052 | 1045 STEEL | 0.37 | 0.34 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 10 | 3052 | [8 empty] | 365T |  |  | 920 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 2.130 |  | Included |  | Included | 2981 | 60131 | 23-5-423 |  | Direct |  |  |  |  | Yes | [5 empty] | 2 3/16 |  |  | 2.1870 | 2.1860 | 2.1875 | 0.5000 X 0.2500 |  |  |  |  | Yes | Ambient Temp F=70 | Size=4014; Design=5800; Arrangement=8S; % Width=100.0; Discharge=UB; Rotation=CW; CFM=10000; SP=24.00; BHP=49.5; RPM=1780; Max Temp F=120; Effective Wheel Dia=41 3/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=23-5-423; Blades=10; Shaft Dia=2 3/16; Brg Centers=14; Critical Speed RPM=4177; BX=11 7/8; STB=6 3/4; OH=7.21; STH=2.00; Bearing Size=2 3/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=365T; Drive=Direct | Open
418322 | HDX | OK | cbc_qt_run_text | QT RUN-FEA UPDATE.pdf |  |  | 418322 | 6000 | 6195 |  |  | 7S1 | 95.0 | TH | CW | 57 | 86180 | 28.80 | 493.9 | 1788 | 136 | 136 | 0.0597 | 500.0 | 1800 | 26861 | 6 1/4 | 84 | 2658 |  |  |  | 11.12 |  | 4.12 | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 1352 | FIXED | 582 | 364 | 3499 | 1893 | 1045 STEEL | 0.12 | 0.59 |  |  | ASTM A6 XF-100 | 5/16 | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 1/2 |  |  |  | 10 | 1893 | 2790 | [7 empty] | 09 |  | ODP | 7446 |  | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 19.195 | 63.000 |  |  |  | 22752 | 320618 | 19-5-218 | FALK T10 | Direct | Required |  | Yes | Yes | [9 empty] | 3.4370 | 3.4355 |  | 0.8750 X 0.4375 | 113 1/2 | 24 1/8 | 1125 | SK-19-72 | Yes | Ambient Temp F=70 | Size=6000; Design=6195; Arrangement=7S1; % Width=95.0; Discharge=TH; Rotation=CW; CFM=86180; SP=28.80; BHP=493.9; RPM=1788; Max Temp F=136; Effective Wheel Dia=57; Blade Material=ASTM A6 XF-100; Blade Gauge=5/16; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Hub=19-5-218; Coupling=FALK T10; Blades=10; Shaft Dia=6 1/4; Brg Centers=84; Critical Speed RPM=2658; STB=11.12; STH=4.12; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=09; Motor Enclosure=ODP; Drive=Direct | Open
418331 | GENERAL LINE | OK | cbc_qt_run_text | 418331 quote run.txt |  |  | 418331 | 19 | 16A | 4 |  | 1S | 100.0 | BAU | CW | 33 | 10435 | 8.00 | 100.0 | 2540 | 70 | 70 | 0.0750 | 100.0 | 2540 | 21944 | 3 7/16 | 14 | 4180 | 44 5/16 | 14.25 | 14 1/4 | 12 5/8 |  |  | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 1554 | FIXED | 447 | 0 | 89 | 2688 | 1045 STEEL | 0.11 | 0.26 |  |  | ASTM CQ HRS A36 | 1/4 | [7 empty] | 6 | 2688 | 16830 | [5 empty] | 7.5 | 3.4 | [15 empty] | Belt | Required |  |  |  | Yes | [5 empty] | 3 7/16 | [11 empty] | Ambient Temp F=90 | Size=19; Design=16A; Arrangement=1S; % Width=100.0; Discharge=BAU; Rotation=CW; Class=4; CFM=10435; SP=8.00; BHP=100.0; RPM=2540; Max Temp F=70; Effective Wheel Dia=33; Blade Material=ASTM CQ HRS A36; Blade Gauge=1/4; Blades=6; Shaft Dia=3 7/16; Brg Centers=14; Critical Speed RPM=4180; BX=14 1/4; STB=12 5/8; OH=14.25; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Drive=Belt | Open
418342 | GENERAL LINE | CHECK VISION | pdf_vision | QT RUN REV A-BLADE LINERS.pdf |  |  | 418342 | 26 | 16A LS | 4 |  | 88 | 70.0 | 70.0 PCT DISCH TH | ROT CCW | 45 1/8 | 30000 | 10.00 | 138.0 | 1770 | 70 | 500 | 0.0417 | 200.0 | 1800 | 22089 | 3 15/16 | 16 | 2934 | 44 3/16 | 15.75 | 17 | 8 1/2 | 153 |  | 3 15/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | -365 | FIXED | 1068 | 0 |  | 1840 | 1045 STEEL | 0.28 | 0.17 |  |  | ASTM A572 X-TEN | 3/8 | ASTM A572 X-TEN | 3/8 |  |  | PLAIN FIRMEX | 1/4 | STEEL | 6 | 1840 | 18440 | [20 empty] | STEEL | FALK T10, SIZE 1110T, BORE 3.938 | Direct |  |  |  |  | Yes | [5 empty] | 3 15/16 | [11 empty] | Ambient Temp F=70 | Size=26; Design=16A LS; Arrangement=88; % Width=70.0; Discharge=70.0 PCT DISCH TH; Rotation=ROT CCW; Class=4; CFM=30000; SP=10.00; BHP=138.0; RPM=1770; Max Temp F=500; Effective Wheel Dia=45 1/8; Blade Material=ASTM A572 X-TEN; Blade Gauge=3/8; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=3/8; Liner Material=PLAIN FIRMEX; Liner Gauge=1/4; Wheel Material=STEEL; Hub=STEEL; Coupling=FALK T10, SIZE 1110T, BORE 3.938; Blades=6; Shaft Dia=3 15/16; Brg Centers=16; Critical Speed RPM=2934; BX=17; STB=8 1/2; OH=15.75; Bearing Size=3 15/16; Bearing Series=LINK BELT SERIES 6800; Drive=Direct | Open
418343 | GENERAL LINE | OK | pdf_vision | QT RUN.pdf |  |  | SN 418343 | 26 | 16A LS | 4 | LS | 8S | 70.0 | PCT DISCH UB | ROT CW | 45 1/8 | 30000 | 15.00 | 205.9 | 1770 | 150 | 200 | 0.0623 | 250.0 | 1800 | 21265 | 3 15/16 | 16 | 3007 | 7/16, OH 15.75, BX 17 1/4, STB 9 3/4, TG&P 157 | 15.75 | 17 1/4 | 9 3/4 | 157 |  | 3 15/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | -353 | FIXED | 1061 | 0 | 503 | 1885 | 1045 STEEL | 0.27 | 0.21 |  |  | ASTM A572 X-TEN | 3/8 | ASTM A572 X-TEN | 1/4 |  |  | PLAIN FIRMEX | 1/8 | STEEL | 6 | 1885 | 18940 | [20 empty] | 3 15/16 | FALK T10, SIZE 1110T, BORE 3.9938 | DRIVE-FLOAT |  |  |  |  | Yes | [5 empty] | 3 15/16 | [11 empty] | Ambient Temp F=70 | Size=26; Design=16A LS; Fan Type=LS; Arrangement=8S; % Width=70.0; Discharge=PCT DISCH UB; Rotation=ROT CW; Class=4; CFM=30000; SP=15.00; BHP=205.9; RPM=1770; Max Temp F=200; Effective Wheel Dia=45 1/8; Blade Material=ASTM A572 X-TEN; Blade Gauge=3/8; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Liner Material=PLAIN FIRMEX; Liner Gauge=1/8; Wheel Material=STEEL; Hub=3 15/16; Coupling=FALK T10, SIZE 1110T, BORE 3.9938; Blades=6; Shaft Dia=3 15/16; Brg Centers=16; Critical Speed RPM=3007; BX=17 1/4; STB=9 3/4; OH=15.75; Bearing Size=3 15/16; Bearing Series=LINK BELT SERIES 6800; Drive=DRIVE-FLOAT | Open
418421 | GENERAL LINE | OK | cbc_qt_run_text | Damper QT Run.txt | DAMPER |  | 418421 | 22.250 | 6195 |  |  | 4S | 105.0 | UB | CW | 21 1/8 | 11375 | 16.00 | 37.1 | 3550 | 70 | 70 | 0.0750 | 40.0 | 3600 | 19922 | [8 empty] | 1.62 | [15 empty] | ASTM A6 XF-100 | 3/16 | ASTM A6 XF-100 | 3/16 | ASTM A6 XF-100 | 3/16 |  |  |  | 10 | 5687 | 7110 | 79 | 73 | 36 | 3.72 | 4.62 |  |  | 324TS |  |  | 687 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 2.753 |  | Not included |  | Yes |  |  | 19-5-1055 |  | Motor mounted | Required |  | Yes |  | Yes | [7 empty] | Q2 BUSHING 1 7/8 | [9 empty] | Ambient Temp F=70 | Size=22.250; Design=6195; Arrangement=4S; % Width=105.0; Discharge=UB; Rotation=CW; CFM=11375; SP=16.00; BHP=37.1; RPM=3550; Max Temp F=70; Effective Wheel Dia=21 1/8; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=3/16; Backplate Material=ASTM A6 XF-100; Backplate Gauge=3/16; Hub=19-5-1055; Blades=10; STH=1.62; Motor Frame=324TS; Drive=Motor mounted | Open
418477 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 418477 | 4900 | 5800 |  |  | 4S | 100.0 | UB | CW | 49 | 19000 | 26.00 | 103.9 | 1785 | 143 | 150 | 0.0550 | 125.0 | 1800 | 23091 | 2 7/16 | 16 | 3776 | 33 1/16 | 7.29 | 13 1/8 | 7 3/8 |  | 2.38 | 2 7/16 | LINK BELT SERIES 300 | 400000 | FIXED | -43 | FIXED | 415 | 277 | 483 | 1861 | 1045 STEEL | 0.64 | 0.42 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 10 | 2539 |  | 280 | 277 | 483 | 4.04 | 5.95 |  |  | 444T |  |  | 1515 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 3.155 |  | Not included |  | Included | 4222 | 68406 | 49-5-145- | FALK G20 | Motor mounted |  |  |  | Yes | Yes | [5 empty] | 3 3/8 |  |  | 2.4370 | 2.4360 | 2.4375 | 0.6250 X 0.3125 |  |  |  |  | Yes | Ambient Temp F=70 | Size=4900; Design=5800; Arrangement=4S; % Width=100.0; Discharge=UB; Rotation=CW; CFM=19000; SP=26.00; BHP=103.9; RPM=1785; Max Temp F=150; Effective Wheel Dia=49; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=49-5-145-; Coupling=FALK G20; Blades=10; Shaft Dia=2 7/16; Brg Centers=16; Critical Speed RPM=3776; BX=13 1/8; STB=7 3/8; OH=7.29; STH=2.38; Bearing Size=2 7/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=444T; Drive=Motor mounted | Open
418517 | GENERAL LINE | OK | d64_wheel_construction | 350-25-2243 D64 Wheel Construction (Inner Ring).xlsx | [103 empty] | Fan Size=222; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=80000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.25 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=222; Outer Ring Thickness=0.25; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=80000 | Open
418564 | HDX | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 418564 | 5414 | 5500 |  |  | 8S | 100.0 | TH | CW | 55 | 39205 | 29.70 | 248.0 | 1785 | 232 | 250 | 0.0549 | 250.0 | 1800 | 25918 | 3 11/16 | 16 | 3281 | 42 5/8 | 13.46 | 20 15/16 | 10 |  | 2.19 | 3 11/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -286 | FLOAT | 941 | 0 | 1120 | 1822 | 1045 STEEL | 0.35 | 0.26 |  |  | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A572 X-TEN | 5/16 |  |  |  | 16 | 2009 | [8 empty] | 449T |  |  | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 19 IN. CENTERS | 7.701 |  | Included | 3.00 | Included | 7929 | 120889 | 23-5-424 | FALK T10 | Direct |  | Required |  | Yes | Yes | [5 empty] | 3 7/16 |  |  | 3.4370 | 3.4355 | 3.4375 | 0.8750 X 0.4375 |  |  |  | SK-55-11 | Yes | Ambient Temp F=70 | Size=5414; Design=5500; Arrangement=8S; % Width=100.0; Discharge=TH; Rotation=CW; CFM=39205; SP=29.70; BHP=248.0; RPM=1785; Max Temp F=250; Effective Wheel Dia=55; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=23-5-424; Coupling=FALK T10; Blades=16; Shaft Dia=3 11/16; Brg Centers=16; Critical Speed RPM=3281; BX=20 15/16; STB=10; OH=13.46; STH=2.19; Bearing Size=3 11/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=449T; Drive=Direct | Open
418677 | GENERAL LINE | OK | cbc_qt_run_text | qt run.txt |  |  | 418677 | 4900 | 6195 |  |  | 8S | 95.0 | UB | CW | 46 9/16 | 56250 | 15.00 | 184.4 | 1780 | 100 | 100 | 0.0670 | 200.0 | 1800 | 21936 | 3 7/16 | 16 | 3472 | 38 1/4 | 10.94 | 21 1/16 | 9 3/8 | 101 | 2.94 | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -271 | FLOAT | 938 | 0 | 1171 | 2148 | 1045 STEEL | 0.28 | 0.23 | 33 |  | ASTM A6 XF-100 | 3/16 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 3/8 |  |  |  | 10 | 2148 | 3090 | [7 empty] | 447T |  |  | 2280 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 12.790 |  | Included |  | Included | 6845 | 84716 | 19-5-289 | FALK T10 | Direct | Required |  | Yes |  | Yes | [5 empty] | 3 7/16 |  |  | 3.4370 | 3.4355 | 3.4375 | 0.8750 X 0.4375 |  |  |  | SK-19-72 | Yes | Ambient Temp F=70; Discharge Height (A)=55 13/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=36 1/2; Base Width (F)=66 1/4; Shaft Height (H)=51 5/8; Total Vert Height (TV)=88 1/8; Max Right of CL to Hsg (RH)=39 15/16; Max Left of CL to Disch (LH)=57 13/16; Base Flange to CL (D)=89 9/16; Drive End of Shaft to CL (K)=46 15/16; Mtg Flange to CL (LR)=19 1/2 | Size=4900; Design=6195; Arrangement=8S; % Width=95.0; Discharge=UB; Rotation=CW; CFM=56250; SP=15.00; BHP=184.4; RPM=1780; Max Temp F=100; Effective Wheel Dia=46 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Hub=19-5-289; Coupling=FALK T10; Blades=10; Shaft Dia=3 7/16; Brg Centers=16; Critical Speed RPM=3472; BX=21 1/16; STB=9 3/8; OH=10.94; STH=2.94; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=33; Motor Frame=447T; Drive=Direct | Open
418698 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.txt |  |  | 418698 | 3000 | 6105 |  |  | 1S | 95.0 | TAD | CCW | 31 1/2 | 16775 | 28.00 | 93.7 | 2652 | 80 | 150 | 0.0723 | 100.0 | 2670 | 22019 | 2 11/16 | 12 | 5409 | 31 15/16 | 8.68 | 14 1/8 | 11 3/16 | 51 | 1.94 | 2 11/16 | LINK BELT SERIES 6800 | 186000 | FLOAT | 1856 | FIXED | 564 | 191 | 152 | 3200 | 1045 STEEL | 0.19 | 0.63 | 20 1/8 |  | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 |  |  |  | 10 | 3330 | 5260 | [5 empty] | 5.8 | 3.6 |  |  |  |  | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 4.769 |  | Included |  | Included | 1431 | 39014 | 19-5-26 |  | Belt | Required |  |  |  | Yes | [5 empty] | 2 11/16 | [10 empty] | Yes | Ambient Temp F=70; Discharge Height (A)=34 1/8; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=35 3/8; Base Width (F)=44 1/4; Shaft Height (H)=33 7/16; Total Vert Height (TV)=65 9/16; Max Right of CL to Hsg (RH)=27 1/8; Max Left of CL to Disch (LH)=50 9/16; Base Flange to CL (D)=30 5/16; Drive End of Shaft to CL (K)=37 5/16; Mtg Flange To Cl (LL)=11 31/32 | Size=3000; Design=6105; Arrangement=1S; % Width=95.0; Discharge=TAD; Rotation=CCW; CFM=16775; SP=28.00; BHP=93.7; RPM=2652; Max Temp F=150; Effective Wheel Dia=31 1/2; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=19-5-26; Blades=10; Shaft Dia=2 11/16; Brg Centers=12; Critical Speed RPM=5409; BX=14 1/8; STB=11 3/16; OH=8.68; STH=1.94; Bearing Size=2 11/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=20 1/8; Drive=Belt | Open
418744 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 418744 | 2700 | 6195 |  |  | 4S1 | 100.0 | DB | CW | 25 5/8 | 17692 | 23.50 | 81.8 | 3550 | 100 | 100 | 0.0684 | 100.0 | 3600 | 24175 | [8 empty] | 1.69 | [15 empty] | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 |  |  |  | 10 | 4184 | 6700 | 141 | 159 | 103 | 4.17 | 4.19 |  |  | 405TS |  |  | 1260 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 3.951 | 30.000 | Not included |  |  | 2729 | 57545 | 19-5-1056 |  | Motor mounted |  |  | Yes |  | Yes | [7 empty] | Q2 BUSHING 2 1/8 |  |  |  |  | 54 | 11 3/8 | 10 |  |  | Ambient Temp F=70 | Size=2700; Design=6195; Arrangement=4S1; % Width=100.0; Discharge=DB; Rotation=CW; CFM=17692; SP=23.50; BHP=81.8; RPM=3550; Max Temp F=100; Effective Wheel Dia=25 5/8; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=19-5-1056; Blades=10; STH=1.69; Motor Frame=405TS; Drive=Motor mounted | Open
418745 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 418745 | 3612 | 5800 |  |  | 4S | 100.0 | BH | CW | 40 | 8286 | 23.00 | 43.4 | 1780 | 70 | 70 | 0.0750 | 50.0 | 1800 | 18850 | 1 11/16 | 12 | 3274 | 25 | 6.13 | 10 3/8 | 5 1/2 | 16 | 1.81 | 1 11/16 | LINK BELT SERIES 300 | 400000 | FIXED | -64 | FIXED | 257 | 102 | 210 | 2335 | 1045 STEEL | 0.55 | 0.47 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 10 | 3273 |  | 167 | 102 | 210 | 3.13 | 4.01 |  |  | 326T |  |  | 610 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 1.754 |  | Not included |  |  | 1956 | 49262 | 23-5-423 | FALK G20 | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 1/8 |  |  | 1.6870 | 1.6860 | 1.6875 | 0.3750 X 0.1875 |  |  |  |  | Yes | Ambient Temp F=70 | Size=3612; Design=5800; Arrangement=4S; % Width=100.0; Discharge=BH; Rotation=CW; CFM=8286; SP=23.00; BHP=43.4; RPM=1780; Max Temp F=70; Effective Wheel Dia=40; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=23-5-423; Coupling=FALK G20; Blades=10; Shaft Dia=1 11/16; Brg Centers=12; Critical Speed RPM=3274; BX=10 3/8; STB=5 1/2; OH=6.13; STH=1.81; Bearing Size=1 11/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=326T; Drive=Motor mounted | Open
418796 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN-UPDATED FOR 3 INCH SHAFT EXTENSION.txt |  |  | 418796 | 2700 | 6105 |  |  | 1S | 105.0 | UB | CW | 28 3/8 | 17000 | 23.00 | 77.6 | 2836 | 70 | 70 | 0.0750 | 100.0 | 2866 | 21272 | 2 7/16 | 12 | 5113 | 30 11/16 | 8.22 | 13 5/16 | 10 1/8 | 41 | 1.69 | 2 7/16 | LINK BELT SERIES 6800 | 231537 | FLOAT | 1490 | FIXED | 421 | 145 | 104 | 3400 | 1045 STEEL | 0.22 | 0.71 |  |  | ASTM A6 XF-100 | 1/4 | ASTM A6 XF-100 | 1/4 | ASTM A6 XF-100 | 1/4 |  |  |  | 10 | 4595 | 5740 | [5 empty] | 5.4 | 3.7 |  |  |  |  | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 4.031 |  |  |  | Yes | 1019 | 59806 | 19-5-1056 |  | Belt | Required |  | Yes |  | Yes | [7 empty] | Q2 BUSHING 2 7/16 | [8 empty] | Yes | Ambient Temp F=70 | Size=2700; Design=6105; Arrangement=1S; % Width=105.0; Discharge=UB; Rotation=CW; CFM=17000; SP=23.00; BHP=77.6; RPM=2836; Max Temp F=70; Effective Wheel Dia=28 3/8; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=1/4; Backplate Material=ASTM A6 XF-100; Backplate Gauge=1/4; Hub=19-5-1056; Blades=10; Shaft Dia=2 7/16; Brg Centers=12; Critical Speed RPM=5113; BX=13 5/16; STB=10 1/8; OH=8.22; STH=1.69; Bearing Size=2 7/16; Bearing Series=LINK BELT SERIES 6800; Drive=Belt | Open
418901 | GENERAL LINE | OK | cbc_qt_run_text | 418901-QT RUN_REF SCROLL GEOMETRY ONLY.txt |  |  | 418901 | 6600 | 1910 |  |  | 3S | 100.0 | BAU | CW |  | 100000 | 4.60 | 115.8 | 686 | 70 | 100 | 0.0750 | 125.0 | 800 | 14915 | 2 15/16 | 63 | 1201 |  |  |  | 7.62 | 146 | 4.94 | 2 15/16 | LINK BELT SERIES 22400 | 400000 | FIXED | 1024 | FIXED | 278 | 416 | 3854 | 845 | 1045 STEEL | 0.77 | 0.59 | 57 7/8 |  | ASTM A1011 CS | 0.075 (14) | ASTM A1011 CS | 0.105 (12) | ASTM CQ HRS A36 | 5/16 |  |  |  | 12 | 845 | 1600 | [11 empty] | 1/4 C.Q. HRS | SK-9-236 MED PRESSURE, 30 IN. CENTERS | 25.923 |  | Included |  |  | 7459 | 111781 | 19-5-1434 | FALK G20 | Direct | [13 empty] | 2.9370 | 2.9355 |  | 0.7500 X 0.3750 |  |  |  |  | Yes | Ambient Temp F=90; Discharge Height (A)=64 1/2; Bottom of Disch to CL (W)=5 5/16; Outlet/Inlet Flange (KK)=3; Discharge Flange to CL (E)=51 3/4; Base Width (F)=91 1/2; Shaft Height (H)=74 7/8; Total Vert Height (TV)=124 7/8; Max Right of CL to Hsg (RH)=59 13/16; Max Left of CL to Disch (LH)=88 1/16; Span (S)=63 5/8; Inboard Brg Center To Cl (SL)=32 1/16; Outboard Brg Center To Cl (SR)=31 9/16; Drive End of Shaft to CL (K)=39 11/16; Outboard End Of Shaft To Cl (M)=34 1/2 | Size=6600; Design=1910; Arrangement=3S; % Width=100.0; Discharge=BAU; Rotation=CW; CFM=100000; SP=4.60; BHP=115.8; RPM=686; Max Temp F=100; Blade Material=ASTM A1011 CS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=5/16; Hub=19-5-1434; Coupling=FALK G20; Blades=12; Shaft Dia=2 15/16; Brg Centers=63; Critical Speed RPM=1201; STB=7.62; STH=4.94; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 22400; Housing Width (N)=57 7/8; Drive=Direct | Open
418941 | HDX | OK | cbc_qt_run_text | QT RUN-CO#1.pdf |  |  | 418941 | 5414 | 5500 |  |  | 4S1 | 100.0 | TH | CW | 52 3/4 | 40738 | 29.56 | 231.4 | 1770 | 175 | 175 | 0.0600 | 250.0 | 1800 | 24858 | 2 11/16 | 16 | 3482 | 34 7/8 | 7.80 | 15 5/16 | 7 7/8 |  | 2.19 | 2 11/16 | LINK BELT SERIES 6800 | 215427 | FIXED | -126 | FLOAT | 673 | 0 | 977 | 2024 | 1045 STEEL | 0.92 | 0.65 |  |  | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A572 X-TEN | 5/16 |  |  |  | 16 | 2024 |  | 444 | 453 | 976 | 3.68 | 6.38 |  |  | 449T |  |  | 3250 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 7.701 |  | Not included |  |  | 9036 | 131562 | 23-5-424 | FALK G20 | Motor mounted |  | Required |  | Yes | Yes | [5 empty] | 3 3/8 |  |  | 2.6870 | 2.6860 | 2.6875 | 0.6250 X 0.3125 | 74 | 23 5/16 | 270 | SK-55-11 | Yes | Ambient Temp F=25 | Size=5414; Design=5500; Arrangement=4S1; % Width=100.0; Discharge=TH; Rotation=CW; CFM=40738; SP=29.56; BHP=231.4; RPM=1770; Max Temp F=175; Effective Wheel Dia=52 3/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=23-5-424; Coupling=FALK G20; Blades=16; Shaft Dia=2 11/16; Brg Centers=16; Critical Speed RPM=3482; BX=15 5/16; STB=7 7/8; OH=7.80; STH=2.19; Bearing Size=2 11/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=449T; Drive=Motor mounted | Open
418941 | HDX | UNRECOGNIZED FORMAT | unknown | FRESH AIR DAMPER QT RUN.doc | DAMPER | [104 empty] | Open
418941 | HDX | UNRECOGNIZED FORMAT | unknown | OUTLET DAMPER QT RUN.doc | DAMPER | [104 empty] | Open
418944 | GENERAL LINE | OK | cbc_qt_run_text | QUOTE RUN.txt |  |  | 418944 | 660 | 51A | 1 |  | 3 |  |  |  |  | 100000 | 4.50 | 91.0 | 650 |  |  |  |  | 728 |  | 4 7/16 | 101 | 885 |  |  |  | 7.69 |  |  | 3 3/16 | LINK BELT SERIES 6800 | 400000 | FIXED | 738 | FLOAT | 691 | 0 | 3460 | 728 | 1045 STEEL | 0.34 | 0.40 | [35 empty] | FALK G20 | Direct | Required | [22 empty] | Size=660; Design=51A; Arrangement=3; Class=1; CFM=100000; SP=4.50; BHP=91.0; RPM=650; Coupling=FALK G20; Shaft Dia=4 7/16; Brg Centers=101; Critical Speed RPM=885; STB=7.69; Bearing Size=3 3/16; Bearing Series=LINK BELT SERIES 6800; Drive=Direct | Open
418998 | HD-PFD-IAF | OK | cbc_qt_run_text | QUOTE RUN.txt |  |  | 418998 | 3612 | 1903 |  | PACKAGED FORCED DRAFT FAN | 4S | 95.0 | UB | CW | 38 5/16 | 20894 | 14.46 | 60.5 | 1770 | 105 | 105 | 0.0686 | 75.0 | 1800 | 18060 | [8 empty] | 2.25 | [15 empty] | ASTM A1011-HSLAS | 0.060 (16) | ASTM A1011-HSLAS | 0.135 (10) | ASTM CQ HRS A36 | 1/4 |  |  |  | 10 | 2543 | 3180 | 197 | 173 | 246 | 4.61 | 4.50 |  |  | 365T |  | TEFC | 1150 | 7 GA C.Q. HRS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 7.071 |  | Not included |  | Yes |  |  | 19-5-1057 |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q1 BUSHING 2 3/8 | [9 empty] | Ambient Temp F=90 | Size=3612; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S; % Width=95.0; Discharge=UB; Rotation=CW; CFM=20894; SP=14.46; BHP=60.5; RPM=1770; Max Temp F=105; Effective Wheel Dia=38 5/16; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Hub=19-5-1057; Blades=10; STH=2.25; Motor Frame=365T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
419066 | GENERAL LINE | OK | d64_wheel_construction | D64 Wheel Construction (Inner Ring)- 350-25-2751.xlsx | [103 empty] | Fan Size=222; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=30000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.1046 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=222; Outer Ring Thickness=0.1046; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=30000 | Open
419099 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 419099 | 4900 | 6195 |  |  | 9H1 | 100.0 | UB | CW | 46 9/16 | 46000 | 13.00 | 123.2 | 1460 | 70 | 70 | 0.0750 | 125.0 | 1800 | 21936 | 3 7/16 | 16 | 3262 | 40 3/8 | 10.72 | 21 3/8 | 12 |  | 2.94 | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 2146 | FIXED | 783 | 432 | 1459 | 1812 | 1045 STEEL | 0.31 | 0.42 | 33 5/8 | 33 1/8 | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/2 |  |  |  | 10 | 2054 | 3700 | [5 empty] | 10.5 | 3.4 | 444T | Z |  | 1515 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 13.033 |  | Included |  |  | 7479 | 116664 | 19-5-289 |  | Belt |  |  | Yes | Yes | Yes | [5 empty] | 3 3/16 | [6 empty] | 88 1/4 | 18 3/4 | 1 | SK-19-72 | Yes | Ambient Temp F=70; Discharge Height (A)=55 13/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=37 3/4; Unitary Base To Cl (LB)=84 1/16; Motor Cl To Fan Cl (LM)=62 1/2; Inlet Box Width (B)=88 1/4; Inlet Box Length To Cl (J)=48 1/4; Shaft Height (H)=54 5/8; Total Vert Height (TV)=102 7/8; Max Right of CL to Hsg (RH)=46 1/8; Max Left of CL to Disch (LH)=57 13/16; Mounting Channel (MA)=1 15/16; Base Flange to CL (D)=42 3/4; Drive End of Shaft to CL (K)=49 3/8; Box Cl To Hsg Cl (P)=38 3/16; Box Width Os (C)=18 3/4; Mtg Flange to CL (LR)=50 9/16 | Size=4900; Design=6195; Arrangement=9H1; % Width=100.0; Discharge=UB; Rotation=CW; CFM=46000; SP=13.00; BHP=123.2; RPM=1460; Max Temp F=70; Effective Wheel Dia=46 9/16; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Hub=19-5-289; Blades=10; Shaft Dia=3 7/16; Brg Centers=16; Critical Speed RPM=3262; BX=21 3/8; STB=12; OH=10.72; STH=2.94; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=33 5/8; Base to CL (F)=33 1/8; Motor Frame=444T; Motor Position=Z; Drive=Belt | Open
419103 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN-FEA UPDATE.pdf |  |  | 419103 | 3300 | 5500 |  |  | 4S | 100.0 | UB | CW | 35 1/4 | 19620 | 53.60 | 198.0 | 3570 | 143 | 150 | 0.0517 | 200.0 | 3600 | 33222 | 2 3/16 | 12 | 5573 | 26 1/16 | 6.59 | 10 9/16 | 6 1/4 |  | 1.31 | 2 3/16 | LINK BELT SERIES 6800 | 219180 | FIXED | -37 | FLOAT | 221 | 0 | 132 | 3796 | 1045 STEEL | 0.69 | 0.47 |  |  | ASTM A240 316L SS | 3/16 | ASTM A240 316L SS | 5/8 | ASTM A240 316L SS | 3/16 |  |  |  | 16 | 3683 |  | 277 | 332 | 303 | 3.68 | 3.51 |  |  | 447TS |  |  | 2280 | 1/4 A240 304L SS | SK-9-236 HI PRESSURE, 18 IN. CENTERS | 2.850 |  | Not included |  | Included | 4329 | 81806 | 23-5-644 | FALK G20 | Motor mounted | Required | Required | Yes | Yes | Yes | [5 empty] | 2 3/8 |  |  | 2.1870 | 2.1860 | 2.1875 | 0.5000 X 0.2500 |  |  |  | SK-55-11 | Yes | Ambient Temp F=70 | Size=3300; Design=5500; Arrangement=4S; % Width=100.0; Discharge=UB; Rotation=CW; CFM=19620; SP=53.60; BHP=198.0; RPM=3570; Max Temp F=150; Effective Wheel Dia=35 1/4; Blade Material=ASTM A240 316L SS; Blade Gauge=3/16; Sideplate Material=ASTM A240 316L SS; Sideplate Gauge=5/8; Backplate Material=ASTM A240 316L SS; Backplate Gauge=3/16; Hub=23-5-644; Coupling=FALK G20; Blades=16; Shaft Dia=2 3/16; Brg Centers=12; Critical Speed RPM=5573; BX=10 9/16; STB=6 1/4; OH=6.59; STH=1.31; Bearing Size=2 3/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=447TS; Drive=Motor mounted | Open
419224 | GENERAL LINE | OK | cbc_qt_run_text | quote run - 11-03-25.pdf |  |  | 419224 | 18-1/4 | 36 | 2 |  | 9 | 100.0 | UB | CCW |  | 5000 | 3.00 | 15.0 | 2152 | 650 | 650 | 0.0750 | 15.0 | 2223 | 11460 | 1 7/16 | 10 | 3148 | 25 3/4 | 7.81 | 12 | 5 3/4 |  | 1.86 | 1 7/16 | LINK BELT SERIES 200 | 41004 | FIXED | 248 | FIXED | 65 | 0 | 16 | 2431 | A240 304 SS | 0.59 | 0.61 |  |  | ASTM A240 304L SS | 0.135 (10) | ASTM A240 304L SS | 0.105 (12) | ASTM A240 304L SS | 0.135 (10) |  |  |  | 12 | 2431 | 5340 | [5 empty] | 7.1 | 3.6 | [13 empty] | 4-5-145 |  | Belt |  |  | Yes |  | Yes | [5 empty] | 1 7/16 | [11 empty] | Ambient Temp F=90 | Size=18-1/4; Design=36; Arrangement=9; % Width=100.0; Discharge=UB; Rotation=CCW; Class=2; CFM=5000; SP=3.00; BHP=15.0; RPM=2152; Max Temp F=650; Blade Material=ASTM A240 304L SS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A240 304L SS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A240 304L SS; Backplate Gauge=0.135 (10); Hub=4-5-145; Blades=12; Shaft Dia=1 7/16; Brg Centers=10; Critical Speed RPM=3148; BX=12; STB=5 3/4; OH=7.81; STH=1.86; Bearing Size=1 7/16; Bearing Series=LINK BELT SERIES 200; Drive=Belt | Open
419280 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 419280 | 5414 | 5500 |  |  | 8S | 100.0 | UB | CW | 50 3/4 | 34438 | 14.00 | 105.5 | 1770 | 750 | 750 | 0.0329 | 125.0 | 1800 | 23915 | 3 15/16 | 16 | 4295 | 40 3/4 | 11.65 | 18 15/16 | 10 1/8 |  | 2.19 | 3 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -180 | FLOAT | 832 | 0 | 929 | 1875 | 1045 STEEL | 0.25 | 0.11 |  |  | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A572 X-TEN | 5/16 |  |  |  | 16 | 1875 | [8 empty] | 444T |  |  | 1515 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 7.701 |  | Included |  | Included | 6189 | 113781 | 23-5-424 | FALK T10 | Direct |  | Required |  | Yes | Yes | [5 empty] | 3 11/16 |  |  | 3.9370 | 3.9355 | 3.9375 | 1.0000 X 0.5000 |  |  |  | SK-55-11 | Yes | Ambient Temp F=70 | Size=5414; Design=5500; Arrangement=8S; % Width=100.0; Discharge=UB; Rotation=CW; CFM=34438; SP=14.00; BHP=105.5; RPM=1770; Max Temp F=750; Effective Wheel Dia=50 3/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 ( 7); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=23-5-424; Coupling=FALK T10; Blades=16; Shaft Dia=3 15/16; Brg Centers=16; Critical Speed RPM=4295; BX=18 15/16; STB=10 1/8; OH=11.65; STH=2.19; Bearing Size=3 15/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=444T; Drive=Direct | Open
419520 | GENERAL LINE | OK | cbc_qt_run_text | 419520 quote run.txt |  |  | 419520 | 24 | B10 |  |  | 9H | 50.0 | BAU | CCW |  | 6239 | 16.00 | 24.9 | 2485 | 100 | 100 | 0.0750 | 30.0 | 2485 | 17198 | 2 7/16 | 17 | 4521 | 39 7/16 | 10.87 | 16 | 8 7/8 |  | 2.50 | 2 7/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 422 | FIXED | 97 | 79 | 36 | 3098 | 1045 STEEL | 0.09 | 0.21 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011 CS | 0.135 (10) |  |  |  | 8 | 3098 | 3720 | [5 empty] | 6.1 | 3.0 | 286T | Z |  | 390 | 10 GA C.Q. HRS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 3.034 | [6 empty] | 4-5-38 |  | Belt |  |  |  |  | Yes | [5 empty] | 2 7/16 | [10 empty] | Yes | Ambient Temp F=70 | Size=24; Design=B10; Arrangement=9H; % Width=50.0; Discharge=BAU; Rotation=CCW; CFM=6239; SP=16.00; BHP=24.9; RPM=2485; Max Temp F=100; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.135 (10); Hub=4-5-38; Blades=8; Shaft Dia=2 7/16; Brg Centers=17; Critical Speed RPM=4521; BX=16; STB=8 7/8; OH=10.87; STH=2.50; Bearing Size=2 7/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=286T; Motor Position=Z; Drive=Belt | Open
419577 | HDX | OK | cbc_qt_run_text | QT RUN-CO#1.pdf |  |  | 419577 | 3612 | 5500 |  |  | 7S1 | 100.0 | TH | CCW | 35 3/4 | 10885 | 16.64 | 35.8 | 1780 | 105 | 105 | 0.0689 | 40.0 | 1800 | 16847 | 2 3/16 | 37 | 3574 |  |  |  | 6.50 |  | 1.50 | 1 15/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 157 | FIXED | 43 | 95 | 148 | 2553 | 1045 STEEL | 0.20 | 0.26 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 16 | 3213 | [8 empty] | 326T |  |  | 762 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 3.477 |  |  |  |  | 3332 | 87470 | 23-5-423 |  | Direct | Required |  |  | Yes | Yes | [8 empty] | 1.9370 | 1.9360 |  | 0.5000 X 0.2500 | 49 3/4 | 15 11/16 | 724 |  | Yes | Ambient Temp F=70 | Size=3612; Design=5500; Arrangement=7S1; % Width=100.0; Discharge=TH; Rotation=CCW; CFM=10885; SP=16.64; BHP=35.8; RPM=1780; Max Temp F=105; Effective Wheel Dia=35 3/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=23-5-423; Blades=16; Shaft Dia=2 3/16; Brg Centers=37; Critical Speed RPM=3574; STB=6.50; STH=1.50; Bearing Size=1 15/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=326T; Drive=Direct | Open
419577 | HDX | UNRECOGNIZED FORMAT | unknown | OD QT RUN.doc | [105 empty] | Open
419623 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.txt |  |  | 419623 | 2000 | 1904 |  | PACKAGED FORCED DRAFT FAN | 4S1 | 90.0 | DB | CW | 22 | 7810 | 15.00 | 26.4 | 3540 | 116 | 116 | 0.0690 | 30.0 | 3600 | 20735 | [8 empty] | 1.25 | [15 empty] | ASTM A1011-HSLAS | 0.048 (18) | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 10 | 4594 | 5740 | 56 | 71 | 20 | 2.31 | 4.25 |  |  | 286T |  | TEFC | 487 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 2.099 |  | Not included |  |  |  |  | 19-5-1055 |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q1 BUSHING 1 7/8 |  |  |  |  | 36 | 7 5/8 | 10 |  |  | Ambient Temp F=90 | Size=2000; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S1; % Width=90.0; Discharge=DB; Rotation=CW; CFM=7810; SP=15.00; BHP=26.4; RPM=3540; Max Temp F=116; Effective Wheel Dia=22; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.048 (18); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.075 (14); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=19-5-1055; Blades=10; STH=1.25; Motor Frame=286T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
419624 | HD-PFD-IAF | OK | cbc_qt_run_text | DAMPER QUOTE RUN.txt | DAMPER |  | 419624 | 3612 | 1904 |  | PACKAGED FORCED DRAFT FAN | 4S1 | 60.0 | DB | CW | 40 1/8 | 16095 | 16.00 | 53.0 | 1775 | 134 | 134 | 0.0669 | 60.0 | 1800 | 18920 | [8 empty] | 2.25 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 1/4 |  |  |  | 10 | 2158 | 2700 | 199 | 197 | 278 | 3.60 | 4.50 |  |  | 364T |  | TEFC | 1043 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 6.206 |  | Not included |  |  |  |  | 19-5-1057 |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q1 BUSHING 2 3/8 |  |  |  |  | 65 3/4 | 13 15/16 | 7 |  |  | Ambient Temp F=90 | Size=3612; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S1; % Width=60.0; Discharge=DB; Rotation=CW; CFM=16095; SP=16.00; BHP=53.0; RPM=1775; Max Temp F=134; Effective Wheel Dia=40 1/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Hub=19-5-1057; Blades=10; STH=2.25; Motor Frame=364T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
419644 | GENERAL LINE | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | 8N419644 | 30 | B10 |  |  | 18 | 100.0 | PCT | CW | 2414 | 30000 | 15.00 | 111.2 | 2360 | 70 | 70 | 0.0750 | 125.0 | 2360 | 20000 | 2 7/16 | 14 | 4176 | 29 15/16 | 8.53 | 16 | 6 1/8 | 40 | 2.94 | 2 7/16 | LINK BELT SERIES 200 | 400000 | FIXED | -66 | FIXED | 297 | 161 | 163 | 2418 | 1045 STEEL | 0.32 | 0.29 |  |  | ASTM A6 XF-100 | 1/4 | ASTM A1011-HSLAS | 0.105 (12) | ASTM A572 X-TEN | 1/4 |  |  | CAST IRON | 12 | 2418 | 4030 | [11 empty] | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | [7 empty] | BORE 2 7/16 | FALK G20, SIZE 1020G, BORE 2.438 | Direct |  |  | Yes |  | Yes | [5 empty] | 2 7/16 | [10 empty] | Yes | Ambient Temp F=90 | Size=30; Design=B10; Arrangement=18; % Width=100.0; Discharge=PCT; Rotation=CW; CFM=30000; SP=15.00; BHP=111.2; RPM=2360; Max Temp F=70; Effective Wheel Dia=2414; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Wheel Material=CAST IRON; Hub=BORE 2 7/16; Coupling=FALK G20, SIZE 1020G, BORE 2.438; Blades=12; Shaft Dia=2 7/16; Brg Centers=14; Critical Speed RPM=4176; BX=16; STB=6 1/8; OH=8.53; STH=2.94; Bearing Size=2 7/16; Bearing Series=LINK BELT SERIES 200; Drive=Direct | Open
419725 | HDX | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 419725 | 5414 | 5500 |  |  | 7S1 | 100.0 | TH | CW | 56 3/4 | 51795 | 34.10 | 383.6 | 1780 | 105 | 120 | 0.0670 | 400.0 | 1800 | 26743 | 3 7/16 | 51 | 3119 |  |  |  | 10.62 |  | 2.19 | 3 3/16 | LINK BELT SERIES 6800 | 222017 | FIXED | 631 | FLOAT | 148 | 0 | 1340 | 1880 | 1045 STEEL | 0.47 | 0.58 |  |  | ASTM A572 X-TEN | 1/4 | ASTM A1011-HSLAS | 0.135 (10) | ASTM A572 X-TEN | 5/16 |  |  |  | 16 | 1880 | [10 empty] | ODP | 3990 | 3/8 C.Q. HRS | SK-9-236 HI PRESSURE, 19 IN. CENTERS | 7.701 |  |  |  |  | 13368 | 189723 | 23-5-424 | FALK T10 | Direct |  |  |  | Yes | [9 empty] | 3.1870 | 3.1855 |  | 0.7500 X 0.3750 | 74 | 23 5/16 | 1125 | SK-55-11 | Yes | Ambient Temp F=70 | Size=5414; Design=5500; Arrangement=7S1; % Width=100.0; Discharge=TH; Rotation=CW; CFM=51795; SP=34.10; BHP=383.6; RPM=1780; Max Temp F=120; Effective Wheel Dia=56 3/4; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=23-5-424; Coupling=FALK T10; Blades=16; Shaft Dia=3 7/16; Brg Centers=51; Critical Speed RPM=3119; STB=10.62; STH=2.19; Bearing Size=3 3/16; Bearing Series=LINK BELT SERIES 6800; Motor Enclosure=ODP; Drive=Direct | Open
419725 | HDX | UNRECOGNIZED FORMAT | unknown | OUTLET DAMPER QT RUN.doc | DAMPER | [104 empty] | Open
419970 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN 419970 FEA UPDATE.docx |  |  | 419970 | 6600 | 6195 |  |  | 9H | 100.0 | BAU | CCW | 62 11/16 | 92497 | 27.00 | 250.0 | 1406 | 70 | 70 | 0.0745 | 300.0 | 1406 | 23079 | 4 15/16 | 22 | 2619 | 53 5/8 | 12.91 | 28 | 16 3/8 |  | 3.69 | 4 15/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 4382 | FIXED | 1600 | 868 | 5352 | 1565 | 1045 STEEL | 0.24 | 0.43 | 45 3/8 | 42 |  | 3/16 |  | 3/16 |  | 1/2 |  |  |  | 10 | 1565 | 2030 | [7 empty] | 449T | Z |  | 2600 | 3/8 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 23.653 |  | Included |  | Yes | 14419 | 227056 | 19-5-218 |  | Belt | Required |  | Yes | Yes | [6 empty] | 4 11/16 | [10 empty] | Yes | Ambient Temp F=70; Discharge Height (A)=75 1/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=3; Discharge Flange to CL (E)=49; Unitary Base To Cl (LB)=95 11/16; Motor Cl To Fan Cl (LM)=73 13/16; Shaft Height (H)=78 9/16; Total Vert Height (TV)=126 5/8; Max Right of CL to Hsg (RH)=89 13/16; Max Left of CL to Disch (LH)=59 1/16; Mounting Channel (MA)=2 1/4; Base Flange to CL (D)=56 7/16; Drive End of Shaft to CL (K)=66 3/8; Mtg Flange to CL (LR)=24 15/16 | Size=6600; Design=6195; Arrangement=9H; % Width=100.0; Discharge=BAU; Rotation=CCW; CFM=92497; SP=27.00; BHP=250.0; RPM=1406; Max Temp F=70; Effective Wheel Dia=62 11/16; Blade Gauge=3/16; Sideplate Gauge=3/16; Backplate Gauge=1/2; Hub=19-5-218; Blades=10; Shaft Dia=4 15/16; Brg Centers=22; Critical Speed RPM=2619; BX=28; STB=16 3/8; OH=12.91; STH=3.69; Bearing Size=4 15/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=45 3/8; Base to CL (F)=42; Motor Frame=449T; Motor Position=Z; Drive=Belt | Open
420033 | GENERAL LINE | OK | cbc_qt_run_text | FA and Outlet Damper QT RUN.pdf | DAMPER |  | 420033 | 3000 | 6195 |  |  | 4S1 | 115.0 | DB | CCW | 28 1/2 | 26085 | 24.00 | 135.9 | 3560 | 146 | 146 | 0.0584 | 150.0 | 3600 | 26861 | [8 empty] | 1.94 | [15 empty] | ASTM A6 XF-100 | 1/4 | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 3/8 |  |  |  | 10 | 4192 | 6270 | 212 | 243 | 185 | 4.73 | 4.19 |  |  | 445TS |  |  | 1785 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 5.125 | 36.500 | Not included |  |  | 4411 | 92222 | 19-5-27 |  | Motor mounted | Required |  | Yes |  | Yes | [5 empty] | 2 3/8 | [6 empty] | 59 1/2 | 12 5/8 | 45 |  |  | Ambient Temp F=70 | Size=3000; Design=6195; Arrangement=4S1; % Width=115.0; Discharge=DB; Rotation=CCW; CFM=26085; SP=24.00; BHP=135.9; RPM=3560; Max Temp F=146; Effective Wheel Dia=28 1/2; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Hub=19-5-27; Blades=10; STH=1.94; Motor Frame=445TS; Drive=Motor mounted | Open
420033 | GENERAL LINE | UNRECOGNIZED FORMAT | unknown | FA DAMPER QT Run.doc | DAMPER | [104 empty] | Open
420033 | GENERAL LINE | UNRECOGNIZED FORMAT | unknown | Outlet Damper QT Run.doc | DAMPER | [104 empty] | Open
420114 | GENERAL LINE | OK | cbc_qt_run_text | quote run.txt |  |  | 420114 | 24 | B10 | 4 |  | 9H | 90.0 | BAU | CW |  | 14000 | 15.00 | 43.6 | 2540 | 100 | 299 | 0.0691 | 50.0 | 2600 | 17994 | 2 3/16 | 12 | 3898 | 33 7/8 | 10.00 | 15 7/8 | 11 | 36 | 2.50 | 2 3/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 872 | FIXED | 260 | 87 | 51 | 2843 | 1045 STEEL | 0.22 | 0.65 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 12 | 2843 | [6 empty] | 6.0 | 3.7 | 326T | W | TEFC | 762 | 10 GA C.Q. HRS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 3.470 | [6 empty] | 19-5-26 |  | Belt |  |  |  |  | Yes | [5 empty] | 2 3/16 | [10 empty] | Yes | Ambient Temp F=90 | Size=24; Design=B10; Arrangement=9H; % Width=90.0; Discharge=BAU; Rotation=CW; Class=4; CFM=14000; SP=15.00; BHP=43.6; RPM=2540; Max Temp F=299; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=19-5-26; Blades=12; Shaft Dia=2 3/16; Brg Centers=12; Critical Speed RPM=3898; BX=15 7/8; STB=11; OH=10.00; STH=2.50; Bearing Size=2 3/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=326T; Motor Position=W; Motor Enclosure=TEFC; Drive=Belt | Open
420217 | GENERAL LINE | OK | d64_wheel_construction | 420217_360-25-2435 D64 Wheel Construction (Inner Ring).xlsx | [103 empty] | Fan Size=200; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=50000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.1345 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=200; Outer Ring Thickness=0.1345; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=50000 | Open
420221 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.txt |  |  | 420221 | 2700 | 1904 |  | PACKAGED FORCED DRAFT FAN | 4S1 | 90.0 | DB | CW | 29 11/16 | 16379 | 18.09 | 68.2 | 2960 | 122 | 150 | 0.0679 | 73.8 | 2975 | 23132 | [8 empty] | 1.69 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 3/8 |  |  |  | 10 | 3951 | 6040 | 209 | 161 | 144 | 3.55 | 6.44 |  |  | 405T |  |  | 1260 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 3.817 |  | Not included |  |  |  |  | 19-5-16 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 7/8 | [6 empty] | 48 1/2 | 10 5/16 | 10 |  |  | Ambient Temp F=90 | Size=2700; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S1; % Width=90.0; Discharge=DB; Rotation=CW; CFM=16379; SP=18.09; BHP=68.2; RPM=2960; Max Temp F=150; Effective Wheel Dia=29 11/16; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Hub=19-5-16; Blades=10; STH=1.69; Motor Frame=405T; Drive=Motor mounted | Open
420351 | GENERAL LINE | OK | d64_wheel_construction | 420351_D64 Wheel Construction (Inner Ring) 363-25-459.xlsx | [103 empty] | Fan Size=182; Max RPM at percent width=max rpm / (sqrt (% width/100)); Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=30000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.25 | Base Gauges=Ratioed Gauges; Number of Blades=9; Fan Size=182; Max RPM at percent width=max rpm / (sqrt (% width/100)); Outer Ring Thickness=0.25; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=30000 | Open
420356 | HDX | OK | cbc_qt_run_text | QT RUN-CO#2.pdf |  |  | 420356 | 5414 | 5500 |  |  | 7S1 | 100.0 | DB | CCW | 54 3/4 | 40909 | 35.68 | 289.0 | 1783 | 167 | 167 | 0.0620 | 300.0 | 1800 | 25800 | 3 11/16 | 55 | 2842 |  |  |  | 9.00 |  | 2.19 | 2 11/16 | LINK BELT SERIES 6800 | 400000 | FIXED | 515 | FLOAT | 184 | 0 | 1117 | 2026 | 1045 STEEL | 0.32 | 0.77 |  |  | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A572 X-TEN | 5/16 |  |  |  | 16 | 2026 | [8 empty] | 449T |  | ODP | 2600 |  | SK-9-236 HI PRESSURE, 19 IN. CENTERS | 7.701 |  | Included | 3.00 |  | 10544 | 200082 | 23-5-424 | FALK T10 | Direct |  |  |  | Yes | [9 empty] | 2.6870 | 2.6860 |  | 0.6250 X 0.3125 | 74 | 23 5/16 | 1125 | SK-55-11 | Yes | Ambient Temp F=70 | Size=5414; Design=5500; Arrangement=7S1; % Width=100.0; Discharge=DB; Rotation=CCW; CFM=40909; SP=35.68; BHP=289.0; RPM=1783; Max Temp F=167; Effective Wheel Dia=54 3/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=23-5-424; Coupling=FALK T10; Blades=16; Shaft Dia=3 11/16; Brg Centers=55; Critical Speed RPM=2842; STB=9.00; STH=2.19; Bearing Size=2 11/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=449T; Motor Enclosure=ODP; Drive=Direct | Open
420374 | HDX | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 420374 | 4900 | 1904 |  |  | 7S1 | 75.0 | TH | CCW | 53 7/8 | 40594 | 29.40 | 244.3 | 1782 | 192 | 200 | 0.0584 | 250.0 | 1800 | 25400 | 4 7/16 | 70 | 2558 |  |  |  | 7.50 |  | 2.94 | 2 11/16 | LINK BELT SERIES 6800 | 400000 | FIXED | 669 | FLOAT | 283 | 0 | 1422 | 1826 | 1045 STEEL | 0.18 | 0.67 |  |  | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM A572 X-TEN | 1/2 |  |  |  | 10 | 1906 | 3000 | [7 empty] | 449T |  |  | 2600 |  | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 11.870 |  | Included | 3.00 |  | 10243 | 193682 | 19-5-219 |  | Direct | Required |  |  | Yes | Yes | [8 empty] | 2.6870 | 2.6860 |  | 0.6250 X 0.3125 | 88 1/4 | 18 3/4 | 1125 | SK-19-72 | Yes | Ambient Temp F=70 | Size=4900; Design=1904; Arrangement=7S1; % Width=75.0; Discharge=TH; Rotation=CCW; CFM=40594; SP=29.40; BHP=244.3; RPM=1782; Max Temp F=200; Effective Wheel Dia=53 7/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Hub=19-5-219; Blades=10; Shaft Dia=4 7/16; Brg Centers=70; Critical Speed RPM=2558; STB=7.50; STH=2.94; Bearing Size=2 11/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=449T; Drive=Direct | Open
420402 | HDX | OK | cbc_qt_run_text | QT RUN-CO#1.pdf |  |  | 420402 | 6300 | 5500 |  |  | 7S1 | 100.0 | TH | CW | 66 1/2 | 80255 | 48.90 | 794.4 | 1785 | 147 | 180 | 0.0633 | 800.0 | 1800 | 31337 | 4 11/16 | 65 | 2661 |  |  |  | 10.00 |  | 2.56 | 3 15/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 889 | FIXED | 361 | 1065 | 2818 | 1900 | 1045 STEEL | 0.41 | 0.66 |  |  | ASTM A6 XF-100 | 3/16 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  |  | 16 | 1958 | [10 empty] | ODP | 5798 | 3/8 C.Q. HRS | SK-9-236 HI PRESSURE, 18 IN. CENTERS | 10.393 |  | Included | 3.00 |  | 19637 | 251996 | 49-5-146- | FALK T10 | Direct |  |  | Yes | Yes | [6 empty] | 4 11/16 |  |  | 3.9370 | 3.9355 |  | 1.0000 X 0.5000 | 86 | 27 1/16 | 1125 | SK-55-11 | Yes | Ambient Temp F=70 | Size=6300; Design=5500; Arrangement=7S1; % Width=100.0; Discharge=TH; Rotation=CW; CFM=80255; SP=48.90; BHP=794.4; RPM=1785; Max Temp F=180; Effective Wheel Dia=66 1/2; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=49-5-146-; Coupling=FALK T10; Blades=16; Shaft Dia=4 11/16; Brg Centers=65; Critical Speed RPM=2661; STB=10.00; STH=2.56; Bearing Size=3 15/16; Bearing Series=LINK BELT SERIES 6800; Motor Enclosure=ODP; Drive=Direct | Open
420410 | GENERAL LINE | OK | cbc_qt_run_text | 420410 qt run.txt |  |  | 420410 | 4412 | 6195 |  |  | 9H | 100.0 | UB | CCW | 42 1/4 | 45000 | 10.00 | 118.9 | 1718 | 70 | 70 | 0.0750 | 125.0 | 1800 | 19922 | 3 3/16 | 14 | 3821 | 36 3/16 | 9.92 | 18 9/16 | 11 1/4 |  | 2.81 | 3 3/16 | LINK BELT SERIES 22400 | 164301 | FIXED | 2152 | FIXED | 600 | 0 | 760 | 1979 | 1045 STEEL | 0.24 | 0.46 | 30 5/8 | 30 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM CQ HRS A36 | 1/4 |  |  |  | 10 | 1979 | 2660 | [5 empty] | 8.9 | 5.2 | 445T | Z |  | 1785 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 10.767 |  |  |  | Included | 5573 | 86314 | 19-5-289 |  | Belt | Required |  | Yes |  | Yes | [5 empty] | 3 3/16 | [9 empty] | SK-19-72 | Yes | Ambient Temp F=70; Discharge Height (A)=50 5/8; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=33 1/4; Unitary Base To Cl (LB)=81 3/16; Motor Cl To Fan Cl (LM)=59 5/8; Shaft Height (H)=50 3/16; Total Vert Height (TV)=83 7/16; Max Right of CL to Hsg (RH)=52 5/8; Max Left of CL to Disch (LH)=36 1/4; Mounting Channel (MA)=1 15/16; Base Flange to CL (D)=36 7/8; Drive End of Shaft to CL (K)=43 13/16; Mtg Flange to CL (LR)=17 7/32 | Size=4412; Design=6195; Arrangement=9H; % Width=100.0; Discharge=UB; Rotation=CCW; CFM=45000; SP=10.00; BHP=118.9; RPM=1718; Max Temp F=70; Effective Wheel Dia=42 1/4; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Hub=19-5-289; Blades=10; Shaft Dia=3 3/16; Brg Centers=14; Critical Speed RPM=3821; BX=18 9/16; STB=11 1/4; OH=9.92; STH=2.81; Bearing Size=3 3/16; Bearing Series=LINK BELT SERIES 22400; Housing Width (N)=30 5/8; Base to CL (F)=30 1/4; Motor Frame=445T; Motor Position=Z; Drive=Belt | Open
420499 | GENERAL LINE | OK | cbc_qt_run_text | qt run-revised for 100% width.txt |  |  | 420499 | 4412 | 6105 |  |  | 8S | 100.0 | TH | CCW | 46 3/4 | 40000 | 19.00 | 146.2 | 1780 | 266 | 347 | 0.0539 | 200.0 | 1800 | 22019 | 3 11/16 | 14 | 3775 | 39 7/16 | 13.23 | 23 1/16 | 10 | 120 | 2.81 | 3 11/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -261 | FLOAT | 830 | 0 | 647 | 1893 | 1045 STEEL | 0.26 | 0.21 | 30 5/8 |  | ASTM A6 XF-100 | 3/16 | ASTM A1011-HSLAS | 0.135 (10) | ASTM A572 X-TEN | 5/16 |  |  |  | 10 | 1893 | 2680 | [7 empty] | 447T |  |  | 2280 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 10.767 |  | Included |  | Included | 6942 | 109967 | 19-5-289 | FALK T10 | Direct | Required |  | Yes |  | Yes | [5 empty] | 3 11/16 |  |  | 3.6870 | 3.6855 | 3.6875 | 0.8750 X 0.4375 |  |  |  |  | Yes | Ambient Temp F=70; Discharge Height (A)=50 5/8; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=33 1/4; Base Width (F)=60 1/2; Shaft Height (H)=42 3/4; Total Vert Height (TV)=95 3/8; Max Right of CL to Hsg (RH)=43 11/16; Max Left of CL to Disch (LH)=33 1/4; Base Flange to CL (D)=88 11/16; Drive End of Shaft to CL (K)=47 1/16; Mtg Flange to CL (LR)=17 7/32 | Size=4412; Design=6105; Arrangement=8S; % Width=100.0; Discharge=TH; Rotation=CCW; CFM=40000; SP=19.00; BHP=146.2; RPM=1780; Max Temp F=347; Effective Wheel Dia=46 3/4; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=19-5-289; Coupling=FALK T10; Blades=10; Shaft Dia=3 11/16; Brg Centers=14; Critical Speed RPM=3775; BX=23 1/16; STB=10; OH=13.23; STH=2.81; Bearing Size=3 11/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=30 5/8; Motor Frame=447T; Drive=Direct | Open
420500 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN-REVISED FOR 100% WIDTH.txt |  |  | 420500 | 4412 | 6105 |  |  | 8S | 100.0 | TH | CW | 46 3/4 | 40000 | 19.00 | 146.2 | 1780 | 266 | 347 | 0.0539 | 200.0 | 1800 | 22019 | 3 11/16 | 14 | 3775 | 39 7/16 | 13.23 | 23 1/16 | 10 | 120 | 2.81 | 3 11/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -261 | FLOAT | 830 | 0 | 647 | 1893 | 1045 STEEL | 0.26 | 0.21 | 30 5/8 |  | ASTM A6 XF-100 | 3/16 | ASTM A1011-HSLAS | 0.135 (10) | ASTM A572 X-TEN | 5/16 |  |  |  | 10 | 1893 | 2680 | [7 empty] | 447T |  |  | 2280 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 10.767 |  | Included |  | Included | 6942 | 109967 | 19-5-289 | FALK T10 | Direct | Required |  | Yes |  | Yes | [5 empty] | 3 11/16 |  |  | 3.6870 | 3.6855 | 3.6875 | 0.8750 X 0.4375 |  |  |  |  | Yes | Ambient Temp F=70; Discharge Height (A)=50 5/8; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=33 1/4; Base Width (F)=60 1/2; Shaft Height (H)=42 3/4; Total Vert Height (TV)=95 3/8; Max Right of CL to Hsg (RH)=33 1/4; Max Left of CL to Disch (LH)=43 11/16; Base Flange to CL (D)=88 11/16; Drive End of Shaft to CL (K)=47 1/16; Mtg Flange to CL (LR)=17 7/32 | Size=4412; Design=6105; Arrangement=8S; % Width=100.0; Discharge=TH; Rotation=CW; CFM=40000; SP=19.00; BHP=146.2; RPM=1780; Max Temp F=347; Effective Wheel Dia=46 3/4; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=19-5-289; Coupling=FALK T10; Blades=10; Shaft Dia=3 11/16; Brg Centers=14; Critical Speed RPM=3775; BX=23 1/16; STB=10; OH=13.23; STH=2.81; Bearing Size=3 11/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=30 5/8; Motor Frame=447T; Drive=Direct | Open
420525 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 420525 | 3000 | 6195 |  |  | 4S1 | 50.0 | TH | CW | 28 1/2 | 11000 | 35.00 | 84.5 | 3570 | 70 | 70 | 0.0750 | 100.0 | 3600 | 26861 | [8 empty] | 1.94 | [15 empty] | ASTM A1011-HSLAS | 0.135 (10) | ASTM CQ HRS A36 | 1/4 | ASTM CQ HRS A36 | 1/4 |  |  |  | 10 | 3675 | 10430 | 142 | 243 | 115 | 3.33 | 4.19 |  |  | 405TS |  | TEFC | 1575 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 3.999 |  | Not included |  |  | 3575 | 52001 | 19-5-27 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 1/8 | [6 empty] | 54 | 11 3/8 | 1 |  |  | Ambient Temp F=90 | Size=3000; Design=6195; Arrangement=4S1; % Width=50.0; Discharge=TH; Rotation=CW; CFM=11000; SP=35.00; BHP=84.5; RPM=3570; Max Temp F=70; Effective Wheel Dia=28 1/2; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM CQ HRS A36; Sideplate Gauge=1/4; Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Hub=19-5-27; Blades=10; STH=1.94; Motor Frame=405TS; Motor Enclosure=TEFC; Drive=Motor mounted | Open
420529 | HD-PFD-IAF | OK | cbc_qt_run_text | 420529_317-26-635RP Qt Run.txt |  |  | 420529 | 3000 | 1904 |  |  | 4S | 85.0 | TH | CW | 33 | 10400 | 13.50 | 27.3 | 1801 | 70 | 70 | 0.0750 | 30.0 | 1801 | 15560 | [8 empty] | 1.94 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 1/4 |  |  |  | 10 | 2876 | 3600 | 146 | 90 | 140 | 3.63 | 4.44 |  |  | 286T |  | ODP | 390 | 10 GA C.Q. HRS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 4.591 |  | Not included |  | Yes | 1213 | 25117 | 19-5-1056 |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q2 BUSHING 1 7/8 | [9 empty] | Ambient Temp F=70 | Size=3000; Design=1904; Arrangement=4S; % Width=85.0; Discharge=TH; Rotation=CW; CFM=10400; SP=13.50; BHP=27.3; RPM=1801; Max Temp F=70; Effective Wheel Dia=33; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Hub=19-5-1056; Blades=10; STH=1.94; Motor Frame=286T; Motor Enclosure=ODP; Drive=Motor mounted | Open
420547 | GENERAL LINE | OK | cbc_qt_run_text | QUOTE RUN.txt |  |  | 420547 | 3000 | 6195 |  |  | 4S1 | 90.0 | UB | CW | 28 1/2 | 27300 | 20.00 | 131.6 | 3550 | 70 | 70 | 0.0750 | 150.0 | 3600 | 26861 | [8 empty] | 1.94 | [15 empty] | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 |  |  |  | 10 | 3808 | 6210 | 170 | 243 | 149 | 4.44 | 4.19 |  |  | 445TS |  | TEFC | 2231 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 4.680 | 36.500 | Not included |  |  | 4732 | 58166 | 19-5-27 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 2 3/8 | [6 empty] | 65 3/4 | 13 15/16 | 1 |  |  | Ambient Temp F=90 | Size=3000; Design=6195; Arrangement=4S1; % Width=90.0; Discharge=UB; Rotation=CW; CFM=27300; SP=20.00; BHP=131.6; RPM=3550; Max Temp F=70; Effective Wheel Dia=28 1/2; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=19-5-27; Blades=10; STH=1.94; Motor Frame=445TS; Motor Enclosure=TEFC; Drive=Motor mounted | Open
420597 | HDX | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 420597 | 6600 | 1910 |  |  | 7S1 | 100.0 | TH | CCW |  | 123323 | 11.26 | 286.0 | 1185 | 425 | 500 | 0.0419 | 300.0 | 1303 | 24293 | 6 3/4 | 105 | 1847 |  |  |  | 9.62 |  | 4.94 | 3 7/16 | LINK BELT SERIES 6800 | 355820 | FIXED | 2144 | FLOAT | 834 | 0 | 7574 | 1318 | 1045 STEEL | 0.19 | 0.58 |  |  | ASTM A1011-HSLAS | 0.105 (12) | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 3/4 |  |  |  | 12 | 1404 | 3430 | [9 empty] | ODP | 4010 |  | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 25.923 | 73.000 |  |  |  | 23703 | 356125 | 19-5-1434 |  | Direct |  |  |  | Yes | [9 empty] | 3.4370 | 3.4355 |  | 0.8750 X 0.4375 | 131 1/2 | 27 7/8 | 1678 |  | Yes | Ambient Temp F=70 | Size=6600; Design=1910; Arrangement=7S1; % Width=100.0; Discharge=TH; Rotation=CCW; CFM=123323; SP=11.26; BHP=286.0; RPM=1185; Max Temp F=500; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/4; Hub=19-5-1434; Blades=12; Shaft Dia=6 3/4; Brg Centers=105; Critical Speed RPM=1847; STB=9.62; STH=4.94; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Motor Enclosure=ODP; Drive=Direct | Open
420691 | HD-PFD-IAF | OK | cbc_qt_run_text | 352-25-3602 Quote Run.txt |  |  | 420691 | 3000 | 1904 |  | PACKAGED FORCED DRAFT FAN | 4S | 100.0 | BAU | CW | 33 | 12153 | 11.10 | 27.2 | 1760 | 100 | 100 | 0.0680 | 30.0 | 1800 | 15551 | [8 empty] | 1.94 | [15 empty] | ASTM A1011-HSLAS | 0.060 (16) | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 10 | 2860 |  | 118 | 90 | 109 | 3.92 | 4.44 |  |  | 286T |  | ODP | 390 | 10 GA C.Q. HRS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 4.858 |  | Not included |  | Yes |  |  | 19-5-1056 |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q1 BUSHING 1 7/8 | [9 empty] | Ambient Temp F=90 | Size=3000; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S; % Width=100.0; Discharge=BAU; Rotation=CW; CFM=12153; SP=11.10; BHP=27.2; RPM=1760; Max Temp F=100; Effective Wheel Dia=33; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.075 (14); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=19-5-1056; Blades=10; STH=1.94; Motor Frame=286T; Motor Enclosure=ODP; Drive=Motor mounted | Open
420755 | GENERAL LINE | OK | cbc_qt_run_text | QUOTE RUN.txt |  |  | 420755 | 22.250 | 6195 |  |  | 4S | 100.0 | DB | CCW | 21 1/8 | 11456 | 13.00 | 31.8 | 3528 | 90 | 90 | 0.0720 | 40.0 | 3600 | 19922 | [8 empty] | 1.62 | [15 empty] | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) |  |  |  | 10 | 3793 | 4740 | 53 | 73 | 21 | 3.19 | 4.62 |  |  | 324TS |  | TEFC | 687 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 2.709 |  | Not included |  | Yes |  |  | 19-5-1055 |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q2 BUSHING 1 7/8 | [9 empty] | Ambient Temp F=90 | Size=22.250; Design=6195; Arrangement=4S; % Width=100.0; Discharge=DB; Rotation=CCW; CFM=11456; SP=13.00; BHP=31.8; RPM=3528; Max Temp F=90; Effective Wheel Dia=21 1/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.075 (14); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.105 (12); Hub=19-5-1055; Blades=10; STH=1.62; Motor Frame=324TS; Motor Enclosure=TEFC; Drive=Motor mounted | Open
420755 | GENERAL LINE | UNRECOGNIZED FORMAT | unknown | DAMPER QUOTE RUN.doc | DAMPER | [104 empty] | Open
420771 | HDX | OK | cbc_qt_run_text | QT RUN, REV.A.pdf |  |  | 420771 | 6912 | 5500 |  |  | 7S1 | 100.0 | TH | CW | 73 1/2 | 72738 | 30.00 | 472.2 | 1780 | 800 | 800 | 0.0274 | 500.0 | 1800 | 34636 | 7 1/4 | 74 | 3018 |  |  |  | 11.12 |  | 2.81 | 3 7/16 | LINK BELT SERIES 6800 | 221836 | FIXED | 1712 | FLOAT | 698 | 0 | 6646 | 1988 | 1045 STEEL | 0.19 | 0.64 |  |  | ASTM A6 XF-100 | 3/16 | ASTM A572 X-TEN | 1/2 | ASTM A572 X-TEN | 3/8 |  |  |  | 16 | 1988 | [10 empty] | ODP | 4453 | 3/8 C.Q. HRS | SK-9-236 HI PRESSURE, 18 IN. CENTERS | 12.665 | [6 empty] | 49-5- | FALK T10 | Direct |  | Required | Yes | Yes | [6 empty] | 7 1/4 |  |  | 3.4370 | 3.4355 |  | 0.8750 X 0.4375 | 94 3/4 | 29 7/8 | 270 | SK-55-11 | Yes | Ambient Temp F=70 | Size=6912; Design=5500; Arrangement=7S1; % Width=100.0; Discharge=TH; Rotation=CW; CFM=72738; SP=30.00; BHP=472.2; RPM=1780; Max Temp F=800; Effective Wheel Dia=73 1/2; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/2; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Hub=49-5-; Coupling=FALK T10; Blades=16; Shaft Dia=7 1/4; Brg Centers=74; Critical Speed RPM=3018; STB=11.12; STH=2.81; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Motor Enclosure=ODP; Drive=Direct | Open
420823 | GENERAL LINE | OK | cbc_qt_run_text | quote run IVC torque.txt |  |  | 420823 | 24 | A10 |  |  | 4S | 45.0 | TH | CW |  | 3425 | 7.00 | 5.6 | 1750 | 70 | 150 | 0.0750 | 7.5 | 1800 | 12457 | [8 empty] | 2.50 | [15 empty] | ASTM A1008 HSLAS | 0.060 (16) | ASTM A1011 CS | 0.075 (14) | ASTM A1011 CS | 0.105 (12) |  |  |  | 12 | 3743 | 6260 | 54 | 40 | 28 | 3.87 | 6.13 |  |  | 213T |  | ODP | 145 | 10 GA C.Q. HRS | SK-9-236 LOW PRESSURE, 36 IN. CENTERS | 2.971 |  | Not included |  |  |  |  | 4-5-14 |  | Motor mounted |  |  |  |  | Yes | [5 empty] | 1 3/8 | [11 empty] | Ambient Temp F=70 | Size=24; Design=A10; Arrangement=4S; % Width=45.0; Discharge=TH; Rotation=CW; CFM=3425; SP=7.00; BHP=5.6; RPM=1750; Max Temp F=150; Blade Material=ASTM A1008 HSLAS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.075 (14); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.105 (12); Hub=4-5-14; Blades=12; STH=2.50; Motor Frame=213T; Motor Enclosure=ODP; Drive=Motor mounted | Open
420848 | HDX | CHECK VISION | pdf_vision | QT RUN.pdf |  |  | SK-9-105 | 6000 | DESIGN 5400 |  | RAYMOND BARTLETT SNOW - SYSTEM FAN | ARR 381,100.0 PCT,DISCH TH ,ROT CW ,BOX 0 | 100.0 | TH | CW | 57 1/4 | 40000 | 36.00 | 321.1 | 1780 | 120 | 220 | 0.0577 | 400.0 | 1800 | 26978 | 4 11/16 | 61 5/8 | 2626 |  |  |  | 8.62 |  | 3.88 | 3 3/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 852 | FIXED | 385 | 832 | 2176 | 1835 | 1045 STEEL | 0.25 | 0.64 |  |  | ASTM A572 X-TEN | 0.183 (7) | ASTM A36 XF-100 | 3/16 | ASTM A572 X-TEN | 5/8 | PLAIN FIRMEX | 3/16 | CAST STEEL | 12 | 1835 | [12 empty] | 3/8 C.Q. HRS | SK-9-236 HI PRESSURE, 18 IN. CENTERS | 6.063 | [6 empty] | 19-5-12 | FALK T10, SIZE 1100T, BORE 3 3/16 NOT INCL. | Direct |  |  |  | Yes | [9 empty] | 3.1870 | 3.1855 |  | 0.7500 X 0.3750 | 82 | 23 1/4 | 1125 |  | Yes | Ambient Temp F=90 | Size=6000; Design=DESIGN 5400; Fan Type=RAYMOND BARTLETT SNOW - SYSTEM FAN; Arrangement=ARR 381,100.0 PCT,DISCH TH ,ROT CW ,BOX 0; % Width=100.0; Discharge=TH; Rotation=CW; CFM=40000; SP=36.00; BHP=321.1; RPM=1780; Max Temp F=220; Effective Wheel Dia=57 1/4; Blade Material=ASTM A572 X-TEN; Blade Gauge=0.183 (7); Sideplate Material=ASTM A36 XF-100; Sideplate Gauge=3/16; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/8; Liner Material=PLAIN FIRMEX; Liner Gauge=3/16; Wheel Material=CAST STEEL; Hub=19-5-12; Coupling=FALK T10, SIZE 1100T, BORE 3 3/16 NOT INCL.; Blades=12; Shaft Dia=4 11/16; Brg Centers=61 5/8; Critical Speed RPM=2626; STB=8.62; STH=3.88; Bearing Size=3 3/16; Bearing Series=LINK BELT SERIES 6800; Drive=Direct | Open
420848 | HDX | UNRECOGNIZED FORMAT | unknown | PSID QUOTE RUN.doc | [105 empty] | Open
420864 | HDX | OK | cbc_qt_run_text | qt run.txt |  |  | 420864 | 4900 | 5500 |  |  | 8S1 | 100.0 | TH | CW | 51 | 34133 | 29.80 | 199.3 | 1788 | 155 | 180 | 0.0618 | 250.0 | 1800 | 24033 | 2 15/16 | 16 | 4902 | 35 5/16 | 7.77 | 14 1/8 | 8 7/8 |  | 2.00 | 2 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -49 | FLOAT | 472 | 0 | 593 | 2374 | 1045 STEEL | 0.67 | 0.50 | 20 1/4 |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 16 | 2374 | [8 empty] | 449T |  |  | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 6.293 |  | Included |  |  | 7586 | 113584 | 49-5-145- | FALK T10 | Direct |  |  |  | Yes | Yes | [5 empty] | 2 11/16 |  |  | 2.9370 | 2.9355 | 2.9375 | 0.7500 X 0.3750 | 66 3/4 | 21 1/16 | 1125 |  | Yes | Ambient Temp F=70; Discharge Height (A)=44 3/4; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=39 1/8; Base Width (F)=66 1/4; Inlet Box Width (B)=66 3/4; Inlet Box Length To Cl (J)=47 3/16; Shaft Height (H)=42 11/16; Total Vert Height (TV)=89 7/8; Max Right of CL to Hsg (RH)=39 1/8; Max Left of CL to Disch (LH)=39 15/16; Base Flange to CL (D)=85 5/8; Drive End of Shaft to CL (K)=39; Box Cl To Hsg Cl (P)=20 13/32; Box Width Os (C)=21 1/16; Mtg Flange to CL (LR)=33 15/16 | Size=4900; Design=5500; Arrangement=8S1; % Width=100.0; Discharge=TH; Rotation=CW; CFM=34133; SP=29.80; BHP=199.3; RPM=1788; Max Temp F=180; Effective Wheel Dia=51; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=49-5-145-; Coupling=FALK T10; Blades=16; Shaft Dia=2 15/16; Brg Centers=16; Critical Speed RPM=4902; BX=14 1/8; STB=8 7/8; OH=7.77; STH=2.00; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=20 1/4; Motor Frame=449T; Drive=Direct | Open
420993 | AXIAL | OK | d64_wheel_construction | 376-26-869 D64 Wheel Construction (Inner Ring).xlsx | [103 empty] | Fan Size=200; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=50000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.1345 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=200; Outer Ring Thickness=0.1345; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=50000 | Open
420996 | GENERAL LINE | OK | d64_wheel_construction | 376-26-869 D64 Wheel Construction (Inner Ring).xlsx | [103 empty] | Fan Size=200; Wheel C.O.G. from Back Plate=365; Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=80000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.1875 | Base Gauges=Ratioed Gauges; Wheel C.O.G. from Back Plate=365; Number of Blades=9; Fan Size=200; Outer Ring Thickness=0.1875; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=80000 | Open
421095 | GENERAL LINE | OK | cbc_qt_run_text | qt run.txt |  |  | 421095 | 200 | 51A | 3 |  | 4 |  |  |  |  | 0 | 0.00 | 28.9 | 3600 | [5 empty] | 18555 | [8 empty] | 1.75 | [15 empty] | ASTM A240 304L SS | 0.060 (16) | ASTM A240 304L SS | 0.105 (12) | ASTM A240 304L SS | 0.075 (14) |  |  |  | 8 | 4251 | 6340 | 39 | 53 | 12 | 3.90 | 5.38 |  |  | 254T |  |  | 230 | [9 empty] | 4-5-145 |  | Motor mounted | Required |  | Yes |  | Yes | [5 empty] | 1 5/8 | [11 empty] | Ambient Temp F=90 | Size=200; Design=51A; Arrangement=4; Class=3; CFM=0; SP=0.00; BHP=28.9; RPM=3600; Blade Material=ASTM A240 304L SS; Blade Gauge=0.060 (16); Sideplate Material=ASTM A240 304L SS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A240 304L SS; Backplate Gauge=0.075 (14); Hub=4-5-145; Blades=8; STH=1.75; Motor Frame=254T; Drive=Motor mounted | Open
421115 | HD-PFD-IAF | OK | cbc_qt_run_text | QUOTE RUN.txt |  |  | 421115 | 2700 | 1903 |  | PACKAGED FORCED DRAFT FAN | 4S | 60.0 | UB | CW | 28 3/8 | 8500 | 40.00 | 72.7 | 3550 | 70 | 70 | 0.0724 | 75.0 | 3600 | 26719 | [8 empty] | 1.69 | [15 empty] | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A572 X-TEN | 1/4 |  |  |  | 10 | 4463 | 5580 | 114 | 207 | 76 | 2.93 | 4.19 |  |  | 365T |  | TEFC | 1150 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 3.390 |  | Not included |  | Yes |  |  | 19-5-1056 |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q1 BUSHING 2 3/8 | [9 empty] | Ambient Temp F=90 | Size=2700; Design=1903; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=4S; % Width=60.0; Discharge=UB; Rotation=CW; CFM=8500; SP=40.00; BHP=72.7; RPM=3550; Max Temp F=70; Effective Wheel Dia=28 3/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 ( 7); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=19-5-1056; Blades=10; STH=1.69; Motor Frame=365T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
421139 | HDX | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 421139 | 4900 | 1904 |  |  | 7S1 | 95.0 | TH | CW | 53 7/8 | 58594 | 29.70 | 328.2 | 1785 | 155 | 180 | 0.0615 | 350.0 | 1800 | 25400 | 4 11/16 | 71 | 2548 |  |  |  | 9.38 |  | 2.94 | 3 3/16 | LINK BELT SERIES 6800 | 134454 | FIXED | 853 | FLOAT | 325 | 0 | 1816 | 2004 | 1045 STEEL | 0.20 | 0.55 |  |  | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM CQ HRS A36 | 1/2 |  |  |  | 10 | 2004 | 2690 | [7 empty] | 449T |  |  | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 12.790 | 54.250 | Included |  |  | 10919 | 150172 | 19-5-12 | FALK T10 | Direct |  |  |  | Yes | [9 empty] | 3.1870 | 3.1855 |  | 0.7500 X 0.3750 | 98 | 20 3/4 | 1125 | SK-19-72 | Yes | Ambient Temp F=90 | Size=4900; Design=1904; Arrangement=7S1; % Width=95.0; Discharge=TH; Rotation=CW; CFM=58594; SP=29.70; BHP=328.2; RPM=1785; Max Temp F=180; Effective Wheel Dia=53 7/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 ( 7); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/2; Hub=19-5-12; Coupling=FALK T10; Blades=10; Shaft Dia=4 11/16; Brg Centers=71; Critical Speed RPM=2548; STB=9.38; STH=2.94; Bearing Size=3 3/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=449T; Drive=Direct | Open
421140 | HDX | OK | cbc_qt_run_text | QT RUN, rev.a.pdf |  |  | 421140 | 6600 | 5800 |  |  | 7S1 | 100.0 | UB | CW | 63 1/2 | 47511 | 20.74 | 280.3 | 1770 | 500 | 600 | 0.0388 | 350.0 | 1800 | 29924 | 6 1/4 | 78 | 2547 |  |  |  | 13.94 |  | 3.06 |  |  |  | FIXED | 1014 | FLOAT | 493 | 0 | 2455 | 1819 | 4140 STEEL | 0.14 | 0.45 |  |  | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 5/16 |  |  |  | 10 | 1856 | [10 empty] | ODP | 2632 |  | SK-9-236 HI PRESSURE, 18 IN. CENTERS | 5.693 |  | Included | 4.00 |  | 20544 | 494782 | 49-5- |  | Direct |  |  |  | Yes | [6 empty] | 6 1/4 |  |  | 3.4370 | 3.4355 | 3.4375 | 0.8750 X 0.4375 | 90 1/4 | 28 5/16 | 90 | SK-58-11 | Yes |  | Size=6600; Design=5800; Arrangement=7S1; % Width=100.0; Discharge=UB; Rotation=CW; CFM=47511; SP=20.74; BHP=280.3; RPM=1770; Max Temp F=600; Effective Wheel Dia=63 1/2; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=49-5-; Blades=10; Shaft Dia=6 1/4; Brg Centers=78; Critical Speed RPM=2547; STB=13.94; STH=3.06; Motor Enclosure=ODP; Drive=Direct | Open
421140 | HDX | UNRECOGNIZED FORMAT | unknown | OUTLET DAMPER QT RUN.doc | DAMPER | [104 empty] | Open
421201 | GENERAL LINE | OK | cbc_qt_run_text | QUOTE RUN.txt |  |  | 421201 | 22.250 | 6195 |  |  | 4S | 80.0 | TH | CW | 21 1/8 | 3178 | 1.18 | 0.9 | 1160 | 77 | 77 | 0.0726 | 1.0 | 1200 | 6641 | [8 empty] | 1.62 | [15 empty] | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.075 (14) |  |  |  | 10 | 3486 | 4360 | 46 | 8 | 17 | 2.98 | 4.62 |  |  | 145T |  | TEFC | 56 | 10 GA A607 X-TEN | SK-9-236 LOW PRESSURE, 36 IN. CENTERS | 2.511 |  | Not included |  | Yes |  |  | 19-5-1055 |  | Motor mounted |  |  |  |  | Yes | [7 empty] | Q2 BUSHING 7/8 | [9 empty] | Ambient Temp F=90 | Size=22.250; Design=6195; Arrangement=4S; % Width=80.0; Discharge=TH; Rotation=CW; CFM=3178; SP=1.18; BHP=0.9; RPM=1160; Max Temp F=77; Effective Wheel Dia=21 1/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.075 (14); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.075 (14); Hub=19-5-1055; Blades=10; STH=1.62; Motor Frame=145T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
421237 | HD-PFD-IAF | OK | cbc_qt_run_text | quote run.txt |  |  | 421237 | 2412 | 1904 |  | PACKAGED FORCED DRAFT FAN | 8S | 90.0 | UB | CW | 26 15/16 | 14000 | 28.00 | 80.8 | 3550 | 70 | 70 | 0.0750 | 100.0 | 3600 | 25400 | 1 15/16 | 12 | 5063 | 25 13/16 | 6.37 | 11 3/16 | 6 1/8 | 22 | 1.62 | 1 15/16 | LINK BELT SERIES 300 | 400000 | FIXED | -35 | FIXED | 173 | 160 | 66 | 3888 | 1045 STEEL | 0.33 | 0.31 | 16 1/4 |  | ASTM A1011-HSLAS | 0.048 (18) | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM CQ HRS A36 | 1/4 |  |  |  | 10 | 4064 | 5080 | [7 empty] | 405TS |  | TEFC | 1575 | 10 GA C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 3.153 |  |  |  | Yes |  |  | 19-5-1056 | FALK T10 | Direct |  | Required |  |  | Yes | [7 empty] | Q1 BUSHING 1 15/16 | 1.9370 | 1.9360 | 1.9375 | 0.5000 X 0.2500 |  |  |  |  | Yes | Ambient Temp F=90; Discharge Height (A)=27 15/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=21 1/8; Base Width (F)=37 3/4; Shaft Height (H)=27 1/4; Total Vert Height (TV)=48 3/8; Max Right of CL to Hsg (RH)=20 3/16; Max Left of CL to Disch (LH)=29 13/16; Base Flange to CL (D)=59 1/16; Drive End of Shaft to CL (K)=29 5/16; Mtg Flange to CL (LR)=10 5/8 | Size=2412; Design=1904; Fan Type=PACKAGED FORCED DRAFT FAN; Arrangement=8S; % Width=90.0; Discharge=UB; Rotation=CW; CFM=14000; SP=28.00; BHP=80.8; RPM=3550; Max Temp F=70; Effective Wheel Dia=26 15/16; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.048 (18); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 ( 7); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Hub=19-5-1056; Coupling=FALK T10; Blades=10; Shaft Dia=1 15/16; Brg Centers=12; Critical Speed RPM=5063; BX=11 3/16; STB=6 1/8; OH=6.37; STH=1.62; Bearing Size=1 15/16; Bearing Series=LINK BELT SERIES 300; Housing Width (N)=16 1/4; Motor Frame=405TS; Motor Enclosure=TEFC; Drive=Direct | Open
421275 | GENERAL LINE | OK | d64_wheel_construction | 421275_D64 Wheel Construction (Inner Ring) 367-26-1520 - FP.xlsx | [103 empty] | Fan Size=300; Max RPM at percent width=max rpm / (sqrt (% width/100)); Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=80000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.25 | Base Gauges=Ratioed Gauges; Number of Blades=9; Fan Size=300; Max RPM at percent width=max rpm / (sqrt (% width/100)); Outer Ring Thickness=0.25; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=80000 | Open
421275 | GENERAL LINE | OK | d64_wheel_construction | 421275_D64 Wheel Construction (Inner Ring) 367-26-1520.xlsx | [103 empty] | Fan Size=300; Max RPM at percent width=max rpm / (sqrt (% width/100)); Steel Temperature Derates=Stainless Temperature Derates; Number of Blades=9; Yield Strength=50000; Base Gauges=Ratioed Gauges; Outer Ring Thickness=0.25 | Base Gauges=Ratioed Gauges; Number of Blades=9; Fan Size=300; Max RPM at percent width=max rpm / (sqrt (% width/100)); Outer Ring Thickness=0.25; Steel Temperature Derates=Stainless Temperature Derates; Yield Strength=50000 | Open
421311 | HD-PFD-IAF | OK | cbc_qt_run_text | 421311 qt run - SEE MARKUP VERSION rev A.txt |  |  | 421311 | 3000 | 1904 |  |  | 8S | 90.0 | TH | CW | 33 | 22648 | 24.54 | 117.5 | 2960 | 131 | 131 | 0.0644 | 125.0 | 2978 | 25728 | 2 15/16 | 12 | 5304 | 30 15/16 | 10.05 | 16 3/8 | 7 3/4 | 60 | 1.94 | 2 15/16 | LINK BELT SERIES 300 | 400000 | FIXED | -88 | FIXED | 337 | 247 | 157 | 3176 | 1045 STEEL | 0.16 | 0.14 | 19 3/4 |  | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 5/16 |  |  |  | 10 | 3176 | 4460 | [7 empty] | 447TS |  | TEFC | 2850 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 4.680 | 33.000 |  |  | Yes | 5115 | 72083 | 19-5-26 | FALK T10 | Direct |  | Required |  |  | Yes | [5 empty] | 2 15/16 |  |  | 2.9370 | 2.9355 | 2.9375 | 0.7500 X 0.3750 |  |  |  |  | Yes | Ambient Temp F=90; Discharge Height (A)=34 1/8; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=24 3/8; Base Width (F)=44 1/4; Shaft Height (H)=27 5/8; Total Vert Height (TV)=63 3/4; Max Right of CL to Hsg (RH)=24 3/8; Max Left of CL to Disch (LH)=29 5/8; Base Flange to CL (D)=74 1/2; Drive End of Shaft to CL (K)=36 1/8; Mtg Flange to CL (LR)=12 3/8 | Size=3000; Design=1904; Arrangement=8S; % Width=90.0; Discharge=TH; Rotation=CW; CFM=22648; SP=24.54; BHP=117.5; RPM=2960; Max Temp F=131; Effective Wheel Dia=33; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=5/16; Hub=19-5-26; Coupling=FALK T10; Blades=10; Shaft Dia=2 15/16; Brg Centers=12; Critical Speed RPM=5304; BX=16 3/8; STB=7 3/4; OH=10.05; STH=1.94; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 300; Housing Width (N)=19 3/4; Motor Frame=447TS; Motor Enclosure=TEFC; Drive=Direct | Open
421311 | HD-PFD-IAF | OK | cbc_qt_run_text | quote run.txt |  |  | 421311 | 3000 | 1904 |  |  | 8S1 | 90.0 | TH | CW | 33 | 22648 | 24.54 | 117.5 | 2960 | 131 | 131 | 0.0644 | 125.0 | 2978 | 25728 | 2 3/16 | 12 | 4388 | 28 15/16 | 7.30 | 13 5/8 | 8 1/2 |  | 1.94 | 2 3/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -11 | FLOAT | 257 | 0 | 156 | 3176 | 1045 STEEL | 0.54 | 0.35 | 19 3/4 |  | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 5/16 |  |  |  | 10 | 3176 | 4460 | [7 empty] | 447T |  | TEFC | 2850 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 4.680 | 33.000 |  |  |  | 5943 | 90101 | 19-5-26 | FALK T10 | Direct | Required | Required |  | Yes | Yes | [5 empty] | 1 15/16 |  |  | 2.1870 | 2.1860 | 2.1875 | 0.5000 X 0.2500 | 59 1/2 | 12 5/8 | 1 |  | Yes | Ambient Temp F=90; Discharge Height (A)=34 1/8; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=35 1/2; Base Width (F)=44 1/4; Inlet Box Width (B)=59 1/2; Inlet Box Length To Cl (J)=38 1/8; Shaft Height (H)=27 5/8; Total Vert Height (TV)=65 3/4; Max Right of CL to Hsg (RH)=35 1/2; Max Left of CL to Disch (LH)=31 3/4; Base Flange to CL (D)=76 5/16; Drive End of Shaft to CL (K)=34 1/8; Box Cl To Hsg Cl (P)=15 15/16; Box Width Os (C)=12 5/8; Mtg Flange to CL (LR)=24 3/4 | Size=3000; Design=1904; Arrangement=8S1; % Width=90.0; Discharge=TH; Rotation=CW; CFM=22648; SP=24.54; BHP=117.5; RPM=2960; Max Temp F=131; Effective Wheel Dia=33; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=5/16; Hub=19-5-26; Coupling=FALK T10; Blades=10; Shaft Dia=2 3/16; Brg Centers=12; Critical Speed RPM=4388; BX=13 5/8; STB=8 1/2; OH=7.30; STH=1.94; Bearing Size=2 3/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=19 3/4; Motor Frame=447T; Motor Enclosure=TEFC; Drive=Direct | Open
421312 | HD-PFD-IAF | OK | cbc_qt_run_text | 421311 qt run - SEE MARKUP VERSION.txt |  |  | 421311 | 3000 | 1904 |  |  | 8S | 90.0 | TH | CW | 33 | 22648 | 24.54 | 117.5 | 2960 | 131 | 131 | 0.0644 | 125.0 | 2978 | 25728 | 2 15/16 | 12 | 8152 | 27 15/16 | 7.05 | 13 3/8 | 7 3/4 | 54 | 1.94 | 2 15/16 | LINK BELT SERIES 300 | 400000 | FIXED | -41 | FIXED | 281 | 247 | 157 | 3176 | 1045 STEEL | 0.15 | 0.14 | 19 3/4 |  | ASTM A1011-HSLAS | 0.075 (14) | ASTM A1011-HSLAS | 0.105 (12) | ASTM CQ HRS A36 | 5/16 |  |  |  | 10 | 3176 | 4460 | [7 empty] | 447TS |  | TEFC | 2850 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 4.680 | 33.000 |  |  | Yes | 5076 | 71484 | 19-5-26 | FALK T10 | Direct |  | Required |  |  | Yes | [5 empty] | 2 15/16 |  |  | 2.9370 | 2.9355 | 2.9375 | 0.7500 X 0.3750 |  |  |  |  | Yes | Ambient Temp F=90; Discharge Height (A)=34 1/8; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=24 3/8; Base Width (F)=44 1/4; Shaft Height (H)=27 5/8; Total Vert Height (TV)=63 3/4; Max Right of CL to Hsg (RH)=24 3/8; Max Left of CL to Disch (LH)=29 5/8; Base Flange to CL (D)=71 1/2; Drive End of Shaft to CL (K)=33 1/8; Mtg Flange to CL (LR)=12 3/8 | Size=3000; Design=1904; Arrangement=8S; % Width=90.0; Discharge=TH; Rotation=CW; CFM=22648; SP=24.54; BHP=117.5; RPM=2960; Max Temp F=131; Effective Wheel Dia=33; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.075 (14); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM CQ HRS A36; Backplate Gauge=5/16; Hub=19-5-26; Coupling=FALK T10; Blades=10; Shaft Dia=2 15/16; Brg Centers=12; Critical Speed RPM=8152; BX=13 3/8; STB=7 3/4; OH=7.05; STH=1.94; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 300; Housing Width (N)=19 3/4; Motor Frame=447TS; Motor Enclosure=TEFC; Drive=Direct | Open
421337 | GENERAL LINE | OK | cbc_qt_run_text | quote run new.txt |  |  | 421337 | 150 | 51A | 1 |  | 3 |  |  |  |  | 0 | 0.00 | 3.8 | 3246 |  |  |  |  | 4657 | 12375 | 1 7/16 | 15 | 11663 |  |  |  | 6.11 | 12 | 1.31 | 1 7/16 | LINK BELT SERIES 200 | 400000 | FIXED | 66 | FIXED | 7 | 0 | 3 | 4657 | 1045 STEEL | 0.05 | 0.09 |  |  | ASTM A1008 HSLAS | 0.048 (18) | ASTM A1011 CS | 0.048 (18) | ASTM A1011 CS | 0.075 (14) |  |  |  | 8 | 4657 | 13020 | [5 empty] | 5.9 | [14 empty] | 4-5-33 |  | Belt | Required | [9 empty] | 1 7/16 | [11 empty] | Ambient Temp F=90 | Size=150; Design=51A; Arrangement=3; Class=1; CFM=0; SP=0.00; BHP=3.8; RPM=3246; Blade Material=ASTM A1008 HSLAS; Blade Gauge=0.048 (18); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.048 (18); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.075 (14); Hub=4-5-33; Blades=8; Shaft Dia=1 7/16; Brg Centers=15; Critical Speed RPM=11663; STB=6.11; STH=1.31; Bearing Size=1 7/16; Bearing Series=LINK BELT SERIES 200; Drive=Belt | Open
421395 | GENERAL LINE | OK | cbc_qt_run_text | 421395_339-26-1324 Rev 2 Qt Run 60%.txt |  |  | 421395 | 17 | 39 |  |  | 9S | 60.0 | TH | CCW | 29 5/8 | 2610 | 9.00 | 6.6 | 1774 | 500 | 500 | 0.0410 | 20.0 | 1774 |  | 1 15/16 | 9 | 3416 | 28 | 10.30 | 10 5/16 | 6 5/8 |  |  | 1 15/16 | LINK BELT SERIES 200 | 400000 | FIXED | 97 | FIXED | 137 | 0 | 35 | 2277 | A240 304 SS | 0.30 | 0.40 | [10 empty] | A240 304L SS | 6 | 2277 | [6 empty] | 8.6 | 3.0 | [15 empty] | Belt |  |  | Yes |  | Yes | [5 empty] | 1 15/16 | [11 empty] | Ambient Temp F=70 | Size=17; Design=39; Arrangement=9S; % Width=60.0; Discharge=TH; Rotation=CCW; CFM=2610; SP=9.00; BHP=6.6; RPM=1774; Max Temp F=500; Effective Wheel Dia=29 5/8; Wheel Material=A240 304L SS; Blades=6; Shaft Dia=1 15/16; Brg Centers=9; Critical Speed RPM=3416; BX=10 5/16; STB=6 5/8; OH=10.30; Bearing Size=1 15/16; Bearing Series=LINK BELT SERIES 200; Drive=Belt | Open
421396 | HDX | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 421396 | 5414 | 5800 |  |  | 7S1 | 100.0 | TH | CCW | 52 3/4 | 25866 | 26.26 | 150.8 | 1786 | 105 | 105 | 0.0500 | 200.0 | 2047 | 28269 | 3 7/16 | 54 | 2697 |  |  |  | 8.75 |  | 2.50 | 2 7/16 | LINK BELT SERIES 6800 | 400000 | FIXED | 449 | FLOAT | 168 | 0 | 899 | 2157 | 1045 STEEL | 0.25 | 0.64 |  |  | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A572 X-TEN | 5/16 |  |  |  | 10 | 2288 | [8 empty] | 447T |  |  | 2280 | 1/2 C.Q. HRS | SK-9-236 HI PRESSURE, 18 IN. CENTERS | 3.842 |  |  |  |  | 14007 | 216238 | 49-5-145- | FALK T10 | Direct |  |  |  | Yes | Yes | [5 empty] | 3 7/16 |  |  | 2.4370 | 2.4360 |  | 0.6250 X 0.3125 | 74 1/8 | 23 5/16 | 1125 | SK-58-11 | Yes | Ambient Temp F=70 | Size=5414; Design=5800; Arrangement=7S1; % Width=100.0; Discharge=TH; Rotation=CCW; CFM=25866; SP=26.26; BHP=150.8; RPM=1786; Max Temp F=105; Effective Wheel Dia=52 3/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=49-5-145-; Coupling=FALK T10; Blades=10; Shaft Dia=3 7/16; Brg Centers=54; Critical Speed RPM=2697; STB=8.75; STH=2.50; Bearing Size=2 7/16; Bearing Series=LINK BELT SERIES 6800; Motor Frame=447T; Drive=Direct | Open
421457 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 421457 | 4900 | 5800 |  |  | 4S | 100.0 | TH | CW | 50 | 21916 | 33.20 | 156.9 | 1789 | 70 | 100 | 0.0717 | 200.0 | 1800 | 23562 | 2 7/16 | 16 | 3716 | 33 3/16 | 7.31 | 13 1/8 | 7 1/2 |  | 2.38 | 2 7/16 | LINK BELT SERIES 300 | 400000 | FIXED | -47 | FIXED | 426 | 288 | 521 | 1822 | 1045 STEEL | 0.91 | 0.63 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.179 ( 7) |  |  |  | 10 | 2529 |  | 288 | 288 | 520 | 4.06 | 5.95 |  |  | 447T |  |  | 2280 | 5/16 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 3.155 |  | Not included |  | Included | 5660 | 89642 | 49-5-145- | FALK G20 | Motor mounted |  |  |  | Yes | Yes | [5 empty] | 3 3/8 |  |  | 2.4370 | 2.4360 | 2.4375 | 0.6250 X 0.3125 |  |  |  | SK-58-11 | Yes | Ambient Temp F=70 | Size=4900; Design=5800; Arrangement=4S; % Width=100.0; Discharge=TH; Rotation=CW; CFM=21916; SP=33.20; BHP=156.9; RPM=1789; Max Temp F=100; Effective Wheel Dia=50; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.179 ( 7); Hub=49-5-145-; Coupling=FALK G20; Blades=10; Shaft Dia=2 7/16; Brg Centers=16; Critical Speed RPM=3716; BX=13 1/8; STB=7 1/2; OH=7.31; STH=2.38; Bearing Size=2 7/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=447T; Drive=Motor mounted | Open
421459 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 421459 | 4014 | 6195 |  |  | 9H | 100.0 | UB | CW | 38 1/4 | 33300 | 22.00 | 139.3 | 2148 | 70 | 95 | 0.0710 | 200.0 | 2148 | 21503 | 3 7/16 | 14 | 5250 | 38 1/16 | 9.98 | 18 7/16 | 12 5/8 | 100 | 2.50 | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 2772 | FIXED | 823 | 280 | 460 | 2200 | 1045 STEEL | 0.21 | 0.67 | 27 3/4 | 27 1/2 | ASTM A6 XF-100 | 3/16 | ASTM A572 X-TEN | 3/16 | ASTM A572 X-TEN | 5/16 |  |  |  | 10 | 2540 | 3690 | [5 empty] | 7.1 | 4.6 | 447T | Z |  | 2280 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 8.828 |  | Included |  | Included | 5224 | 65207 | 19-5-16 |  | Belt |  |  | Yes |  | Yes | [5 empty] | 3 7/16 | [10 empty] | Yes | Ambient Temp F=70; Discharge Height (A)=45 13/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=30; Unitary Base To Cl (LB)=78 7/16; Motor Cl To Fan Cl (LM)=56 7/8; Shaft Height (H)=46 1/16; Total Vert Height (TV)=76 1/16; Max Right of CL to Hsg (RH)=32 7/8; Max Left of CL to Disch (LH)=47 13/16; Mounting Channel (MA)=1 15/16; Base Flange to CL (D)=37 13/16; Drive End of Shaft to CL (K)=45 1/16; Mtg Flange to CL (LR)=15 25/32 | Size=4014; Design=6195; Arrangement=9H; % Width=100.0; Discharge=UB; Rotation=CW; CFM=33300; SP=22.00; BHP=139.3; RPM=2148; Max Temp F=95; Effective Wheel Dia=38 1/4; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=3/16; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=5/16; Hub=19-5-16; Blades=10; Shaft Dia=3 7/16; Brg Centers=14; Critical Speed RPM=5250; BX=18 7/16; STB=12 5/8; OH=9.98; STH=2.50; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=27 3/4; Base to CL (F)=27 1/2; Motor Frame=447T; Motor Position=Z; Drive=Belt | Open
421462 | HD-PFD-IAF | OK | cbc_qt_run_text | QT RUN-CO#1.pdf |  |  | 421462 | 3000 | 5800 |  |  | 4S | 100.0 | BH | CW | 28 1/2 | 9894 | 31.80 | 79.6 | 3550 | 100 | 100 | 0.0681 | 100.0 | 3600 | 26861 | 1 11/16 | 12 | 4973 | 24 5/8 | 5.42 | 9 | 5 1/2 |  | 1.38 | 1 11/16 | LINK BELT SERIES 300 | 400000 | FIXED | -20 | FIXED | 138 | 136 | 53 | 3939 | 1045 STEEL | 0.81 | 0.48 |  |  | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) | ASTM A1011-HSLAS | 0.135 (10) |  |  |  | 10 | 4408 |  | 92 | 136 | 53 | 2.42 | 3.62 |  |  | 405TS |  |  | 1260 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 19 IN. CENTERS | 1.172 |  | Not included |  | Included | 2345 | 40141 | 23-5-423 | FALK G20 | Motor mounted |  | Required |  | Yes | Yes | [5 empty] | 2 1/8 |  |  | 1.6870 | 1.6860 | 1.6875 | 0.3750 X 0.1875 |  |  |  |  | Yes | Ambient Temp F=70 | Size=3000; Design=5800; Arrangement=4S; % Width=100.0; Discharge=BH; Rotation=CW; CFM=9894; SP=31.80; BHP=79.6; RPM=3550; Max Temp F=100; Effective Wheel Dia=28 1/2; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.135 (10); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.135 (10); Backplate Material=ASTM A1011-HSLAS; Backplate Gauge=0.135 (10); Hub=23-5-423; Coupling=FALK G20; Blades=10; Shaft Dia=1 11/16; Brg Centers=12; Critical Speed RPM=4973; BX=9; STB=5 1/2; OH=5.42; STH=1.38; Bearing Size=1 11/16; Bearing Series=LINK BELT SERIES 300; Motor Frame=405TS; Drive=Motor mounted | Open
421473 | GENERAL LINE | OK | cbc_qt_run_text | 421473 quote run.txt |  |  | 421473 | 37 | 16A | 3 |  | 9H | 100.0 | TH | CW | 64 3/8 | 34000 | 21.00 | 184.4 | 963 | 70 | 95 | 0.0710 | 200.0 | 963 |  | 3 7/16 | 29 | 1315 | 65 15/16 | 21.12 | 21 1/8 | 11 5/8 | 174 |  | 3 7/16 | LINK BELT SERIES 22400 | 253649 | FIXED | 2847 | FIXED | 637 | 0 | 1146 | 1095 | 1045 STEEL | 0.51 | 0.74 | [10 empty] | A569 HRS | 6 | 1120 | [6 empty] | 15.9 | 10.3 | [15 empty] | Belt |  |  |  |  | Yes | [5 empty] | 3 7/16 | [11 empty] | Ambient Temp F=70 | Size=37; Design=16A; Arrangement=9H; % Width=100.0; Discharge=TH; Rotation=CW; Class=3; CFM=34000; SP=21.00; BHP=184.4; RPM=963; Max Temp F=95; Effective Wheel Dia=64 3/8; Wheel Material=A569 HRS; Blades=6; Shaft Dia=3 7/16; Brg Centers=29; Critical Speed RPM=1315; BX=21 1/8; STB=11 5/8; OH=21.12; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 22400; Drive=Belt | Open
421496 | HDX | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 421496 | 4900 | 1904 |  |  | 7S1 | 95.0 | TH | CW | 53 7/8 | 54438 | 31.50 | 318.7 | 1770 | 151 | 180 | 0.0631 | 350.0 | 1800 | 25400 | 4 11/16 | 69 | 2574 |  |  |  | 11.12 |  | 2.94 | 3 3/16 | LINK BELT SERIES 6800 | 124877 | FIXED | 948 | FLOAT | 314 | 0 | 1816 | 2004 | 1045 STEEL | 0.20 | 0.55 |  |  | ASTM A1011-HSLAS | 0.105 (12) | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM A572 X-TEN | 1/2 |  |  |  | 10 | 2004 | 2690 | [9 empty] | ODP | 4800 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 20 IN. CENTERS | 12.790 |  |  |  |  | 13711 | 157417 | 19-5-12 | FALK T10 | Direct |  |  |  | Yes | [9 empty] | 3.1870 | 3.1855 |  | 0.7500 X 0.3750 | 88 1/4 | 18 3/4 | 1125 | SK-19-72 | Yes | Ambient Temp F=70 | Size=4900; Design=1904; Arrangement=7S1; % Width=95.0; Discharge=TH; Rotation=CW; CFM=54438; SP=31.50; BHP=318.7; RPM=1770; Max Temp F=180; Effective Wheel Dia=53 7/8; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.105 (12); Sideplate Material=ASTM A1011-HSLAS; Sideplate Gauge=0.179 ( 7); Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/2; Hub=19-5-12; Coupling=FALK T10; Blades=10; Shaft Dia=4 11/16; Brg Centers=69; Critical Speed RPM=2574; STB=11.12; STH=2.94; Bearing Size=3 3/16; Bearing Series=LINK BELT SERIES 6800; Motor Enclosure=ODP; Drive=Direct | Open
421507 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 421507 | 3000 | 6105 |  |  | 4S1 | 45.0 | TH | CW | 31 1/2 | 12689 | 38.00 | 100.6 | 3570 | 95 | 95 | 0.0627 | 125.0 | 3600 | 29688 | [8 empty] | 1.94 | [15 empty] | ASTM A6 XF-100 | 3/16 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 |  |  |  | 10 | 4562 | 10670 | 145 | 348 | 118 | 3.22 | 4.94 |  |  | 444TS |  |  | 1515 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 19 IN. CENTERS | 3.910 |  | Not included |  |  | 3627 | 58311 | 19-5-27 |  | Motor mounted |  |  | Yes |  | Yes | [5 empty] | 2 3/8 |  | Q2 BUSHING |  |  |  |  | 54 | 11 3/8 | 1 |  |  | Ambient Temp F=29 | Size=3000; Design=6105; Arrangement=4S1; % Width=45.0; Discharge=TH; Rotation=CW; CFM=12689; SP=38.00; BHP=100.6; RPM=3570; Max Temp F=95; Effective Wheel Dia=31 1/2; Blade Material=ASTM A6 XF-100; Blade Gauge=3/16; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=1/4; Hub=19-5-27; Blades=10; STH=1.94; Motor Frame=444TS; Drive=Motor mounted | Open
421563 | GENERAL LINE | OK | cbc_qt_run_text | qt run.txt |  |  | 421563 | 4014 | 6195 |  |  | 4S1 | 105.0 | UB | CW | 38 1/4 | 30000 | 14.00 | 84.0 | 1770 | 70 | 150 | 0.0750 | 100.0 | 1800 | 18019 | [8 empty] | 2.50 | [15 empty] | ASTM A1011-HSLAS | 0.179 ( 7) | ASTM CQ HRS A36 | 1/4 | ASTM CQ HRS A36 | 1/4 |  |  |  | 10 | 1929 | 2960 | 302 | 197 | 463 | 6.32 | 6.38 |  |  | 405T |  | TEFC | 1575 | 7 GA C.Q. HRS | SK-9-236 MED PRESSURE, 24 IN. CENTERS | 8.988 |  | Not included |  |  | 4632 | 72319 | 19-5-16 |  | Motor mounted | Required |  |  |  | Yes | [5 empty] | 2 7/8 | [6 empty] | 73 | 15 1/2 | 7 |  |  | Ambient Temp F=90 | Size=4014; Design=6195; Arrangement=4S1; % Width=105.0; Discharge=UB; Rotation=CW; CFM=30000; SP=14.00; BHP=84.0; RPM=1770; Max Temp F=150; Effective Wheel Dia=38 1/4; Blade Material=ASTM A1011-HSLAS; Blade Gauge=0.179 ( 7); Sideplate Material=ASTM CQ HRS A36; Sideplate Gauge=1/4; Backplate Material=ASTM CQ HRS A36; Backplate Gauge=1/4; Hub=19-5-16; Blades=10; STH=2.50; Motor Frame=405T; Motor Enclosure=TEFC; Drive=Motor mounted | Open
421572 | GENERAL LINE | OK | cbc_qt_run_text | quote run 6-17-26.txt |  |  | 421572 | 19 | 16A | 4 |  | 9H | 100.0 | UB | CW | 33 | 12500 | 12.00 | 45.7 | 1673 | 103 | 103 | 0.0690 | 50.0 | 1673 | 14454 | 2 11/16 | 20 | 2422 | 44 1/4 | 12.19 | 12 3/16 | 9 1/8 | 71 |  | 2 11/16 | LINK BELT SERIES 22400 | 400000 | FIXED | 685 | FIXED | 342 | 0 | 171 | 1823 | 1045 STEEL | 0.23 | 0.28 |  |  | ASTM A572 X-TEN | 3/8 |  |  |  |  | PLAIN FIRMEX | 1/4 |  | 6 | 1823 | 11460 | [5 empty] | 9.1 | 3.0 | [15 empty] | Belt |  |  |  |  | Yes | 3/4 | AISI 1026 HFSM | 1/2 | ASTM CQ HRS A36 | ASTM C1018 | 2 11/16 | 7.00 | [10 empty] | Ambient Temp F=90 | Size=19; Design=16A; Arrangement=9H; % Width=100.0; Discharge=UB; Rotation=CW; Class=4; CFM=12500; SP=12.00; BHP=45.7; RPM=1673; Max Temp F=103; Effective Wheel Dia=33; Blade Material=ASTM A572 X-TEN; Blade Gauge=3/8; Liner Material=PLAIN FIRMEX; Liner Gauge=1/4; Blades=6; Shaft Dia=2 11/16; Brg Centers=20; Critical Speed RPM=2422; BX=12 3/16; STB=9 1/8; OH=12.19; Bearing Size=2 11/16; Bearing Series=LINK BELT SERIES 22400; Drive=Belt | Open
421579 | GENERAL LINE | OK | cbc_qt_run_text | QT RUN.txt |  |  | 421579 | 3300 | 6195 |  |  | 9H | 100.0 | TH | CCW | 31 3/8 | 22500 | 18.00 | 78.3 | 2465 | 70 | 95 | 0.0714 | 100.0 | 2585 | 21216 | 2 15/16 | 12 | 5119 | 35 3/8 | 8.64 | 15 3/8 | 12 | 68 | 2.12 | 2 15/16 | LINK BELT SERIES 6800 | 400000 | FLOAT | 1534 | FIXED | 457 | 183 | 267 | 3000 | 1045 STEEL | 0.17 | 0.47 | 22 3/4 | 23 7/8 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM CQ HRS A36 | 3/8 |  |  |  | 10 | 3131 | 6130 | [5 empty] | 6.2 | 3.0 | 405T | W |  | 1260 | 7 GA C.Q. HRS | SK-9-236 HI PRESSURE, 22 IN. CENTERS | 5.934 |  | Included |  | Included | 3205 | 46700 | 19-5-16 |  | Belt | Required |  | Yes |  | Yes | [5 empty] | 2 15/16 | [10 empty] | Yes | Ambient Temp F=41; Discharge Height (A)=37 9/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=26 1/8; Unitary Base to CL (RB)=69 13/16; Motor CL to Fan CL (RM)=49 3/16; Shaft Height (H)=35 9/16; Total Vert Height (TV)=75 1/8; Max Right of CL to Hsg (RH)=32 9/16; Max Left of CL to Disch (LH)=26 1/8; Mounting Channel (MA)=2 1/4; Base Flange to CL (D)=31 7/8; Drive End of Shaft to CL (K)=39 3/8; Mtg Flange to CL (LR)=13 5/8 | Size=3300; Design=6195; Arrangement=9H; % Width=100.0; Discharge=TH; Rotation=CCW; CFM=22500; SP=18.00; BHP=78.3; RPM=2465; Max Temp F=95; Effective Wheel Dia=31 3/8; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM CQ HRS A36; Backplate Gauge=3/8; Hub=19-5-16; Blades=10; Shaft Dia=2 15/16; Brg Centers=12; Critical Speed RPM=5119; BX=15 3/8; STB=12; OH=8.64; STH=2.12; Bearing Size=2 15/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=22 3/4; Base to CL (F)=23 7/8; Motor Frame=405T; Motor Position=W; Drive=Belt | Open
421756 | GENERAL LINE | OK | cbc_qt_run_text | 421756 quote run.txt |  |  | 421756 | 4900 | 6105 |  |  | 8S1 | 85.0 | BH | CCW | 51 7/16 | 49616 | 28.00 | 269.9 | 1785 | 100 | 100 | 0.0680 | 300.0 | 1800 | 24245 | 3 7/16 | 16 | 3578 | 37 3/4 | 10.63 | 20 1/2 | 9 3/8 | 100 | 2.94 | 3 7/16 | LINK BELT SERIES 6800 | 400000 | FIXED | -283 | FLOAT | 965 | 0 | 1225 | 2027 | 1045 STEEL | 0.38 | 0.34 | 31 7/8 |  | ASTM A6 XF-100 | 1/4 | ASTM A572 X-TEN | 1/4 | ASTM A572 X-TEN | 3/8 |  |  |  | 10 | 2027 | 3160 | [7 empty] | 449T |  |  | 2600 | 1/4 C.Q. HRS | SK-9-236 HI PRESSURE, 21 IN. CENTERS | 12.354 |  |  |  |  | 9858 | 121657 | 19-5-289 | FALK T10 | Direct | Required |  | Yes | [7 empty] | 3 7/16 | [6 empty] | 88 1/4 | 18 3/4 | 1 | SK-19-72 | Yes | Ambient Temp F=100; Discharge Height (A)=55 13/16; Bottom of Disch to CL (W)=0; Outlet/Inlet Flange (KK)=2; Discharge Flange to CL (E)=49 7/8; Base Width (F)=66 1/4; Inlet Box Width (B)=88 1/4; Inlet Box Length To Cl (J)=43 7/16; Shaft Height (H)=66 9/16; Total Vert Height (TV)=110; Max Right of CL to Hsg (RH)=49 7/8; Max Left of CL to Disch (LH)=48 1/8; Base Flange to CL (D)=92 3/4; Drive End of Shaft to CL (K)=45 7/8; Box Cl To Hsg Cl (P)=25 1/16; Box Width Os (C)=18 3/4; Mtg Flange to CL (LR)=37 7/16 | Size=4900; Design=6105; Arrangement=8S1; % Width=85.0; Discharge=BH; Rotation=CCW; CFM=49616; SP=28.00; BHP=269.9; RPM=1785; Max Temp F=100; Effective Wheel Dia=51 7/16; Blade Material=ASTM A6 XF-100; Blade Gauge=1/4; Sideplate Material=ASTM A572 X-TEN; Sideplate Gauge=1/4; Backplate Material=ASTM A572 X-TEN; Backplate Gauge=3/8; Hub=19-5-289; Coupling=FALK T10; Blades=10; Shaft Dia=3 7/16; Brg Centers=16; Critical Speed RPM=3578; BX=20 1/2; STB=9 3/8; OH=10.63; STH=2.94; Bearing Size=3 7/16; Bearing Series=LINK BELT SERIES 6800; Housing Width (N)=31 7/8; Motor Frame=449T; Drive=Direct | Open
421817 | GENERAL LINE | OK | cbc_qt_run_text | quote run.txt |  |  | 421817 | 150 | 51A | 1 |  | 3 |  |  |  |  | 0 | 0.00 | 3.8 | 3246 |  |  |  |  | 4657 | 12375 | 1 7/16 | 14 | 12148 |  |  |  | 7.38 | 12 | 1.31 | 1 7/16 | LINK BELT SERIES 200 | 400000 | FIXED | 72 | FIXED | 11 | 0 | 3 | 4657 | 1045 STEEL | 0.07 | 0.12 |  |  | ASTM A1008 HSLAS | 0.048 (18) | ASTM A1011 CS | 0.048 (18) | ASTM A1011 CS | 0.075 (14) |  |  |  | 8 | 4657 | 13020 | [5 empty] | 5.9 | [14 empty] | 4-5-33 |  | Belt | [10 empty] | 1 7/16 | [11 empty] | Ambient Temp F=90 | Size=150; Design=51A; Arrangement=3; Class=1; CFM=0; SP=0.00; BHP=3.8; RPM=3246; Blade Material=ASTM A1008 HSLAS; Blade Gauge=0.048 (18); Sideplate Material=ASTM A1011 CS; Sideplate Gauge=0.048 (18); Backplate Material=ASTM A1011 CS; Backplate Gauge=0.075 (14); Hub=4-5-33; Blades=8; Shaft Dia=1 7/16; Brg Centers=14; Critical Speed RPM=12148; STB=7.38; STH=1.31; Bearing Size=1 7/16; Bearing Series=LINK BELT SERIES 200; Drive=Belt | Open
421876 | GENERAL LINE | OK | cbc_qt_run_text | quote run.txt |  |  | 421876 | 17 | 16A | 4 |  | 9H | 100.0 | BH | CCW | 29 5/8 | 9445 | 20.00 | 49.5 | 2122 | 70 | 500 | 0.0750 | 50.0 | 2122 |  | 2 11/16 | 19 | 3081 | 48 9/16 | 14.25 | 14 1/4 | 12 7/16 | 78 |  | 2 11/16 | LINK BELT SERIES 300 | 59485 | FIXED | 907 | FIXED | 213 | 0 | 40 | 2567 | 1045 STEEL | 0.17 | 0.42 | [11 empty] | 6 | 2876 | [6 empty] | 7.2 | 4.5 |  |  | TEFC | [12 empty] | Belt |  |  |  |  | Yes | [5 empty] | 2 11/16 | [11 empty] | Ambient Temp F=90 | Size=17; Design=16A; Arrangement=9H; % Width=100.0; Discharge=BH; Rotation=CCW; Class=4; CFM=9445; SP=20.00; BHP=49.5; RPM=2122; Max Temp F=500; Effective Wheel Dia=29 5/8; Blades=6; Shaft Dia=2 11/16; Brg Centers=19; Critical Speed RPM=3081; BX=14 1/4; STB=12 7/16; OH=14.25; Bearing Size=2 11/16; Bearing Series=LINK BELT SERIES 300; Motor Enclosure=TEFC; Drive=Belt | Open
421939 | HDX | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 421939 | 6600 | 2310B |  |  | 7S1 | 55.0 | BH | CW | 72 5/8 | 40000 | 82.00 | 811.0 | 1793 | 100 | 100 | 0.0591 | 1000.0 | 1800 | 34212 | 4 7/16 | 55 | 2602 |  |  |  | 11.50 |  | 3.00 | 3 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | 993 | FLOAT | 400 | 0 | 4282 | 1858 | 1045 STEEL | 0.54 | 0.75 |  |  | ASTM A572 X-TEN | 1/4 | ASTM A6 XF-100 | 1/4 | ASTM A6 XF-100 | 3/8 |  |  |  | 11 | 2267 | 4520 | [9 empty] | ODP | 7430 | 3/8 C.Q. HRS | SK-9-236 HI PRESSURE, 18 IN. CENTERS | 2.892 |  |  |  |  | 21958 | 296944 | 23-5-425 | FALK T10 | Direct |  | Required | Yes | Yes | [9 empty] | 3.9370 | 3.9355 |  | 1.0000 X 0.5000 | 68 1/8 | 22 1/4 | 90 |  | Yes | Ambient Temp F=70 | Size=6600; Design=2310B; Arrangement=7S1; % Width=55.0; Discharge=BH; Rotation=CW; CFM=40000; SP=82.00; BHP=811.0; RPM=1793; Max Temp F=100; Effective Wheel Dia=72 5/8; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=1/4; Backplate Material=ASTM A6 XF-100; Backplate Gauge=3/8; Hub=23-5-425; Coupling=FALK T10; Blades=11; Shaft Dia=4 7/16; Brg Centers=55; Critical Speed RPM=2602; STB=11.50; STH=3.00; Bearing Size=3 15/16; Bearing Series=LINK BELT SERIES 6800; Motor Enclosure=ODP; Drive=Direct | Open
421940 | HDX | OK | cbc_qt_run_text | QT RUN.pdf |  |  | 421940 | 6600 | 2310B |  |  | 7S1 | 55.0 | BH | CCW | 72 5/8 | 40000 | 82.00 | 811.0 | 1793 | 100 | 100 | 0.0591 | 1000.0 | 1800 | 34212 | 4 7/16 | 55 | 2602 |  |  |  | 11.50 |  | 3.00 | 3 15/16 | LINK BELT SERIES 6800 | 400000 | FIXED | 993 | FLOAT | 400 | 0 | 4282 | 1858 | 1045 STEEL | 0.54 | 0.75 |  |  | ASTM A572 X-TEN | 1/4 | ASTM A6 XF-100 | 1/4 | ASTM A6 XF-100 | 3/8 |  |  |  | 11 | 2267 | 4520 | [9 empty] | ODP | 7430 | 3/8 C.Q. HRS | SK-9-236 HI PRESSURE, 18 IN. CENTERS | 2.892 |  |  |  |  | 21958 | 296944 | 23-5-425 | FALK T10 | Direct |  | Required | Yes | Yes | [9 empty] | 3.9370 | 3.9355 |  | 1.0000 X 0.5000 | 68 1/8 | 22 1/4 | 270 |  | Yes | Ambient Temp F=70 | Size=6600; Design=2310B; Arrangement=7S1; % Width=55.0; Discharge=BH; Rotation=CCW; CFM=40000; SP=82.00; BHP=811.0; RPM=1793; Max Temp F=100; Effective Wheel Dia=72 5/8; Blade Material=ASTM A572 X-TEN; Blade Gauge=1/4; Sideplate Material=ASTM A6 XF-100; Sideplate Gauge=1/4; Backplate Material=ASTM A6 XF-100; Backplate Gauge=3/8; Hub=23-5-425; Coupling=FALK T10; Blades=11; Shaft Dia=4 7/16; Brg Centers=55; Critical Speed RPM=2602; STB=11.50; STH=3.00; Bearing Size=3 15/16; Bearing Series=LINK BELT SERIES 6800; Motor Enclosure=ODP; Drive=Direct | Open
421959 | GENERAL LINE | OK | cbc_qt_run_text | Cascades Wheel Construction REV 2.txt |  |  | 421959 | 33 | 36 | 2 |  | 9H | 110.0 | UB | CCW |  | 19000 | 9.00 | 36.0 | 1597 | 70 | 70 | 0.0750 | 40.0 | 1690 | 15754 | 2 7/16 | 16 | 2513 | 33 15/16 | 11.30 | 19 1/2 | 6 1/8 |  | 3.19 | 2 7/16 | LINK BELT SERIES 200 | 43217 | FIXED | 502 | FIXED | 329 | 0 | 272 | 1690 | A240 316 SS | 0.33 | 0.31 |  |  | ASTM A240 316L SS | 1/4 | ASTM A240 316L SS | 0.105 (12) | ASTM A240 316L SS | 1/4 |  |  |  | 12 | 1690 | 3110 | [5 empty] | 9.6 | 6.1 | [13 empty] | 4-5-156 |  | Belt |  |  | Yes |  | Yes | [5 empty] | 2 7/16 | [11 empty] | Ambient Temp F=70 | Size=33; Design=36; Arrangement=9H; % Width=110.0; Discharge=UB; Rotation=CCW; Class=2; CFM=19000; SP=9.00; BHP=36.0; RPM=1597; Max Temp F=70; Blade Material=ASTM A240 316L SS; Blade Gauge=1/4; Sideplate Material=ASTM A240 316L SS; Sideplate Gauge=0.105 (12); Backplate Material=ASTM A240 316L SS; Backplate Gauge=1/4; Hub=4-5-156; Blades=12; Shaft Dia=2 7/16; Brg Centers=16; Critical Speed RPM=2513; BX=19 1/2; STB=6 1/8; OH=11.30; STH=3.19; Bearing Size=2 7/16; Bearing Series=LINK BELT SERIES 200; Drive=Belt | Open